## InputOutputData
Storage Tank Height | h | 20 | m |  |  | *AC = Additional Catchment |  |  | Rainwater Collection |  |  |  |  | Storage |  |  | Catchment
Distance to Storage Tank | L | 63.9316 | m | [5 empty] | Roof Catchment | Whole roof |  |  | Volume | 36 | m^3 | Chosen | Whole roof
Pipe diameter | D | 0.02 | m |  |  | Measured Cf | 15040 |  | AC* Size | 0 | m |  | Location | x | -45 | Area | 100 | m
Pipe area | A | 0.00031416 | m^2 | [5 empty] | AC Location | x | 1 |  |  | y | -40 | Price | 350 | $
Pipe friction factor | f | 0.05 | [7 empty] | y | 1 |  | Distance up | 63.9316 | m | AC Distance | N/A | m
Loss coefficient | K | 8 | 12 | first one is pump storage, second one is storage house |  |  |  |  | Catchment tank | 1500 | L |  | Height | 20 | m
Pressure from storage | rho g h | 196200 | Pa | for on demand flow rate |  |  |  |  | Cost | 500 | $ |  | Tower | 0 | m
Consumption | C | 432 | L/day | [9 empty] | Cost Storage | 9900 | $
Pressure from storage | rho g h | 196200 | Pa | for pump? | [8 empty] | Cost Water Tower | 0 | $
[9 empty] | Pump | [5 empty] | Filter
|  | Cf | Actual Filter | Filter Life Data [L] |  |  |  |  | Pump applied | Pump C |  |  |  | Location | Up
Filter Size | Present? | [Pa/(m/s)] | Life [L] | Non pre-filter | 5 micron pre | 200 micron pre |  |  | a | -0.0151
1 micron | y | 2511.68 | 20000 | 5000 | 20000 | 15000 |  |  | b | -0.5516
5 micron | y | 1252.832 | 20000 | 10000 |  | 20000 |  |  | c | 356.8
200 micron | y | 62.7168 | 20000 | 20000 |  |  |  |  | A | 0.72
=IF('InputOutputData'!E36="Data 1( |  | 3827.2288 | [6 empty] | B | 0.55
[13 empty] | UV |  |  | OZONE |  |  |  | Chlorine
[10 empty] | Disinfection |  |  |  | 40 | W | Contact Time | 10 | [min] | Contact time | 10 | min
Atrributes |  |  | Weights | Satisfaction |  |  |  |  | UV | 40 | W |  | Initial Cost | 600 | $ | CT_Ozone | 50 | [mg min/L] | CT_Chlorine | 100 | mg min/L
C | 432 | [L/day] | 0.13 | S(C) | 61.7502 |  |  |  | Ozone or Chlorine | Chlorine | 0 |  | Replacement Cost | 80 | $ | Energy for O3 | 2 | [MJ / g] | Solution Percentage | 5 | %
M | 20 | #/day | 0.15 | S(M) | 81.1745 | [7 empty] | MTBF | 365 | days | Initial Cost | 4000 | $ | Initial Cost | 700 | $
Q0 | 28.5869 | L/min | 0.13 | S(Q0) | 56.8079 | [7 empty] | Power | 40 | W |  |  |  | Cost per container | 100 | $
Cr | 44.4404 | %relative to shipping water | 0.22 | S(Cr) | 82.8814 |  |  |  | Energy | Solar |  |  | Max Flow Rate | 35 | LPM |  |  |  | Container size | 3 | kg
E | 14.161 | N/A | 0.07 | S(E) | 61.741
G | 69.1926 | %relative to shipping water | 0.05 | S(G) | 31.1448 |  |  | Solar |  |  |  |  | Batteries | 3 | #
R | 346 | days/year | 0.1 | S(R) | 96.3381 |  | Type | HES-260 |  |  |  |  | Efficiency in | 0.96
U | 0.10862 | %impact relative to worst case | 0.15 | S(U) | 83.0208 |  | Area | 1.6 | m^2 |  |  |  | Efficiency out | 0.96
|  |  |  | Total | 73.7887 |  | Initial Cost | 550 | $ |  |  |  | Energy Storage | 2000 | Wh
[7 empty] | Efficiency | 0.17
[7 empty] | GHG | 496 | kgCO2e
|  | COST |  |  |  |  | Maintenance | 4 | #times
|  | MAINTENANCE |  |  |  |  | Quantity | 4 | #
|  | LAND USE |  |  |  |  | DC Inverter? | Yes |  |  | Generator | no
|  | CONSUMPTION |  |  |  |  | Cost | 2639 | $ |  | Initial Cost | 3250
|  | FLOW RATE |  |  |  |  | Efficiency | 0.92 |  |  | Efficiency | 0.35
UPDATE DISTANCE DOWN | COEFFICEINT DOWN |  | Rainfall Data | 2 |  |  | GHG | 100 | kgCO2e

## Solar Panel
| Solar |  |  |  |  | Solar Intensity | 300 | W/m^2 |  |  | Sunshine Data
Type | HES-260 | [9 empty] | Month | Sunshine
Area | 1.6 | m^2 |  | Batteries | 3 | # |  |  |  |  | [-] | [hours/day]
Initial Cost | 550 | $ |  | Efficiency in | 0.96 | [5 empty] | January | 8.5
Efficiency | 0.17 |  |  | Efficiency out | 0.96 | [5 empty] | February | 10
GHG | 496 | kgCO2e |  | Energy Storage | 2000 | Wh |  |  |  |  | March | 11.8
Maintenance | 4 | #times | [8 empty] | April | 13.6
Quantity | 4 | # | [8 empty] | May | 15.3
[5 empty] | Disinfection | Chlorine |  |  |  |  | June | 16
[11 empty] | July | 15.75
[11 empty] | August | 14.2
[11 empty] | September | 12.5
[11 empty] | October | 10.75
[11 empty] | November | 9
[11 empty] | December | 8.25
Day | Month | Date | Hours of Sunshine | Incident Solar Energy | Energy Generated | E_in | E_Out | E_Needed | E_Total | E_Battery | Days Without Power | Total Days | Total Days without | 9
[-] | [-] | [-] | [hours] | [Whr] | [Whr] | [Whr] | [J] | [Whr] | [Whr] | [Whr] |  | 9
1 | January | 1 | 8.5 | 16320 | 2774.4 | 2663.424 | 10361048.3416 | 2878.069 | -214.645 | 6000
2 | January | 2 | 8.5 | 16320 | 2774.4 | 2663.424 | 6198442.0076 | 1721.7894 | 941.6346 | 5785.355
3 | January | 3 | 8.5 | 16320 | 2774.4 | 2663.424 | 12257989.5882 | 3404.9971 | -741.5731 | 6000
4 | January | 4 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 5258.4269
5 | January | 5 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 4390.1232
6 | January | 6 | 8.5 | 16320 | 2774.4 | 2663.424 | 7813618.2511 | 2170.4495 | 492.9745 | 3521.8196
7 | January | 7 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 4014.7941
8 | January | 8 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 5718.2181
9 | January | 9 | 8.5 | 16320 | 2774.4 | 2663.424 | 5936504.9601 | 1649.0292 | 1014.3948 | 6000
10 | January | 10 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 6000
11 | January | 11 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 6000
12 | January | 12 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 6000
13 | January | 13 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 6000
14 | January | 14 | 8.5 | 16320 | 2774.4 | 2663.424 | 5271937.5421 | 1464.4271 | 1198.9969 | 6000
15 | January | 15 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 6000
16 | January | 16 | 8.5 | 16320 | 2774.4 | 2663.424 | 9593643.1427 | 2664.9009 | -1.4769 | 5131.6963
17 | January | 17 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 5130.2195
18 | January | 18 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 4261.9158
19 | January | 19 | 8.5 | 16320 | 2774.4 | 2663.424 | 7670812.1991 | 2130.7812 | 532.6428 | 3393.6122
20 | January | 20 | 8.5 | 16320 | 2774.4 | 2663.424 | 5271937.5421 | 1464.4271 | 1198.9969 | 3926.255
21 | January | 21 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 5125.2519
22 | January | 22 | 8.5 | 16320 | 2774.4 | 2663.424 | 12432454.3538 | 3453.4595 | -790.0355 | 4256.9482
23 | January | 23 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 3466.9127
24 | January | 24 | 8.5 | 16320 | 2774.4 | 2663.424 | 12714219.5618 | 3531.7277 | -868.3037 | 2598.609
25 | January | 25 | 8.5 | 16320 | 2774.4 | 2663.424 | 7028411.395 | 1952.3365 | 711.0875 | 1730.3054
26 | January | 26 | 8.5 | 16320 | 2774.4 | 2663.424 | 7813618.2511 | 2170.4495 | 492.9745 | 2441.3929
27 | January | 27 | 8.5 | 16320 | 2774.4 | 2663.424 | 7813618.2511 | 2170.4495 | 492.9745 | 2934.3674
28 | January | 28 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 3427.3419
29 | January | 29 | 8.5 | 16320 | 2774.4 | 2663.424 | 3456000 | 960 | 1703.424 | 5130.7659
30 | January | 30 | 8.5 | 16320 | 2774.4 | 2663.424 | 5635364.2432 | 1565.379 | 1098.045 | 6000
31 | January | 31 | 8.5 | 16320 | 2774.4 | 2663.424 | 9500888.9292 | 2639.1358 | 24.2882 | 6000
32 | February | 1 | 10 | 19200 | 3264 | 3133.44 | 10439971.9766 | 2899.9922 | 233.4478 | 6000
33 | February | 2 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 6000
34 | February | 3 | 10 | 19200 | 3264 | 3133.44 | 5635364.2432 | 1565.379 | 1568.061 | 5601.7123
35 | February | 4 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 6000
36 | February | 5 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 5601.7123
37 | February | 6 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 5203.4247
38 | February | 7 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 4805.137
39 | February | 8 | 10 | 19200 | 3264 | 3133.44 | 9862072.8073 | 2739.4647 | 393.9753 | 4406.8494
40 | February | 9 | 10 | 19200 | 3264 | 3133.44 | 8083231.7108 | 2245.3421 | 888.0979 | 4800.8247
41 | February | 10 | 10 | 19200 | 3264 | 3133.44 | 4785381.2883 | 1329.2726 | 1804.1674 | 5688.9226
42 | February | 11 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 6000
43 | February | 12 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 5601.7123
44 | February | 13 | 10 | 19200 | 3264 | 3133.44 | 12714219.5618 | 3531.7277 | -398.2877 | 5203.4247
45 | February | 14 | 10 | 19200 | 3264 | 3133.44 | 4785381.2883 | 1329.2726 | 1804.1674 | 4805.137
46 | February | 15 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
47 | February | 16 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
48 | February | 17 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
49 | February | 18 | 10 | 19200 | 3264 | 3133.44 | 8571429.8312 | 2380.9527 | 752.4873 | 6000
50 | February | 19 | 10 | 19200 | 3264 | 3133.44 | 11512683.7741 | 3197.9677 | -64.5277 | 6000
51 | February | 20 | 10 | 19200 | 3264 | 3133.44 | 5271937.5421 | 1464.4271 | 1669.0129 | 5935.4723
52 | February | 21 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
53 | February | 22 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
54 | February | 23 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
55 | February | 24 | 10 | 19200 | 3264 | 3133.44 | 4785381.2883 | 1329.2726 | 1804.1674 | 6000
56 | February | 25 | 10 | 19200 | 3264 | 3133.44 | 8903029.0583 | 2473.0636 | 660.3764 | 6000
57 | February | 26 | 10 | 19200 | 3264 | 3133.44 | 10745211.681 | 2984.781 | 148.659 | 6000
58 | February | 27 | 10 | 19200 | 3264 | 3133.44 | 5271937.5421 | 1464.4271 | 1669.0129 | 6000
59 | February | 28 | 10 | 19200 | 3264 | 3133.44 | 3456000 | 960 | 2173.44 | 6000
60 | March | 1 | 11.8 | 22656 | 3851.52 | 3697.4592 | 6432849.3732 | 1786.9026 | 1910.5566 | 6000
61 | March | 2 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
62 | March | 3 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
63 | March | 4 | 11.8 | 22656 | 3851.52 | 3697.4592 | 5271937.5421 | 1464.4271 | 2233.0321 | 6000
64 | March | 5 | 11.8 | 22656 | 3851.52 | 3697.4592 | 7028411.395 | 1952.3365 | 1745.1227 | 6000
65 | March | 6 | 11.8 | 22656 | 3851.52 | 3697.4592 | 5936504.9601 | 1649.0292 | 2048.43 | 6000
66 | March | 7 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
67 | March | 8 | 11.8 | 22656 | 3851.52 | 3697.4592 | 5271937.5421 | 1464.4271 | 2233.0321 | 6000
68 | March | 9 | 11.8 | 22656 | 3851.52 | 3697.4592 | 5271937.5421 | 1464.4271 | 2233.0321 | 6000
69 | March | 10 | 11.8 | 22656 | 3851.52 | 3697.4592 | 7813618.2511 | 2170.4495 | 1527.0097 | 6000
70 | March | 11 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12316618.5358 | 3421.2829 | 276.1763 | 6000
71 | March | 12 | 11.8 | 22656 | 3851.52 | 3697.4592 | 10670393.4171 | 2963.9982 | 733.461 | 6000
72 | March | 13 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
73 | March | 14 | 11.8 | 22656 | 3851.52 | 3697.4592 | 5635364.2432 | 1565.379 | 2132.0802 | 6000
74 | March | 15 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
75 | March | 16 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
76 | March | 17 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
77 | March | 18 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
78 | March | 19 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
79 | March | 20 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
80 | March | 21 | 11.8 | 22656 | 3851.52 | 3697.4592 | 3456000 | 960 | 2737.4592 | 6000
81 | March | 22 | 11.8 | 22656 | 3851.52 | 3697.4592 | 10033591.5579 | 2787.1088 | 910.3504 | 6000
82 | March | 23 | 11.8 | 22656 | 3851.52 | 3697.4592 | 11035434.0676 | 3065.3984 | 632.0608 | 6000
83 | March | 24 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
84 | March | 25 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
85 | March | 26 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
86 | March | 27 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
87 | March | 28 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
88 | March | 29 | 11.8 | 22656 | 3851.52 | 3697.4592 | 11175521.9488 | 3104.3117 | 593.1475 | 6000
89 | March | 30 | 11.8 | 22656 | 3851.52 | 3697.4592 | 12714219.5618 | 3531.7277 | 165.7315 | 6000
90 | March | 31 | 11.8 | 22656 | 3851.52 | 3697.4592 | 11706860.1465 | 3251.9056 | 445.5536 | 6000
91 | April | 1 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
92 | April | 2 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
93 | April | 3 | 13.6 | 26112 | 4439.04 | 4261.4784 | 10819093.7566 | 3005.3038 | 1256.1746 | 6000
94 | April | 4 | 13.6 | 26112 | 4439.04 | 4261.4784 | 10594605.0666 | 2942.9459 | 1318.5325 | 6000
95 | April | 5 | 13.6 | 26112 | 4439.04 | 4261.4784 | 5635364.2432 | 1565.379 | 2696.0994 | 6000
96 | April | 6 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
97 | April | 7 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
98 | April | 8 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
99 | April | 9 | 13.6 | 26112 | 4439.04 | 4261.4784 | 8083231.7108 | 2245.3421 | 2016.1363 | 6000
100 | April | 10 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
101 | April | 11 | 13.6 | 26112 | 4439.04 | 4261.4784 | 10892071.6332 | 3025.5755 | 1235.9029 | 6000
102 | April | 12 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
103 | April | 13 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
104 | April | 14 | 13.6 | 26112 | 4439.04 | 4261.4784 | 6747153.4811 | 1874.2093 | 2387.2691 | 6000
105 | April | 15 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
106 | April | 16 | 13.6 | 26112 | 4439.04 | 4261.4784 | 7950904.5817 | 2208.5846 | 2052.8938 | 6000
107 | April | 17 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
108 | April | 18 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
109 | April | 19 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
110 | April | 20 | 13.6 | 26112 | 4439.04 | 4261.4784 | 6318582.9774 | 1755.1619 | 2506.3165 | 6000
111 | April | 21 | 13.6 | 26112 | 4439.04 | 4261.4784 | 5271937.5421 | 1464.4271 | 2797.0513 | 6000
112 | April | 22 | 13.6 | 26112 | 4439.04 | 4261.4784 | 10517810.6602 | 2921.6141 | 1339.8643 | 6000
113 | April | 23 | 13.6 | 26112 | 4439.04 | 4261.4784 | 10594605.0666 | 2942.9459 | 1318.5325 | 6000
114 | April | 24 | 13.6 | 26112 | 4439.04 | 4261.4784 | 7028411.395 | 1952.3365 | 2309.1419 | 6000
115 | April | 25 | 13.6 | 26112 | 4439.04 | 4261.4784 | 3456000 | 960 | 3301.4784 | 6000
116 | April | 26 | 13.6 | 26112 | 4439.04 | 4261.4784 | 8684837.6853 | 2412.4549 | 1849.0235 | 6000
117 | April | 27 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
118 | April | 28 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
119 | April | 29 | 13.6 | 26112 | 4439.04 | 4261.4784 | 12714219.5618 | 3531.7277 | 729.7507 | 6000
120 | April | 30 | 13.6 | 26112 | 4439.04 | 4261.4784 | 9008199.5737 | 2502.2777 | 1759.2007 | 6000
121 | May | 1 | 15.3 | 29376 | 4993.92 | 4794.1632 | 5936504.9601 | 1649.0292 | 3145.134 | 6000
122 | May | 2 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
123 | May | 3 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
124 | May | 4 | 15.3 | 29376 | 4993.92 | 4794.1632 | 12714219.5618 | 3531.7277 | 1262.4355 | 6000
125 | May | 5 | 15.3 | 29376 | 4993.92 | 4794.1632 | 5271937.5421 | 1464.4271 | 3329.7361 | 6000
126 | May | 6 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
127 | May | 7 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
128 | May | 8 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
129 | May | 9 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
130 | May | 10 | 15.3 | 29376 | 4993.92 | 4794.1632 | 5271937.5421 | 1464.4271 | 3329.7361 | 6000
131 | May | 11 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
132 | May | 12 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
133 | May | 13 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
134 | May | 14 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
135 | May | 15 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
136 | May | 16 | 15.3 | 29376 | 4993.92 | 4794.1632 | 4785381.2883 | 1329.2726 | 3464.8906 | 6000
137 | May | 17 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
138 | May | 18 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
139 | May | 19 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
140 | May | 20 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
141 | May | 21 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
142 | May | 22 | 15.3 | 29376 | 4993.92 | 4794.1632 | 4785381.2883 | 1329.2726 | 3464.8906 | 6000
143 | May | 23 | 15.3 | 29376 | 4993.92 | 4794.1632 | 4785381.2883 | 1329.2726 | 3464.8906 | 6000
144 | May | 24 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
145 | May | 25 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
146 | May | 26 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
147 | May | 27 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
148 | May | 28 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
149 | May | 29 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
150 | May | 30 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
151 | May | 31 | 15.3 | 29376 | 4993.92 | 4794.1632 | 3456000 | 960 | 3834.1632 | 6000
152 | June | 1 | 16 | 30720 | 5222.4 | 5013.504 | 10199769.8786 | 2833.2694 | 2180.2346 | 6000
153 | June | 2 | 16 | 30720 | 5222.4 | 5013.504 | 7813618.2511 | 2170.4495 | 2843.0545 | 6000
154 | June | 3 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
155 | June | 4 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
156 | June | 5 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
157 | June | 6 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
158 | June | 7 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
159 | June | 8 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
160 | June | 9 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
161 | June | 10 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
162 | June | 11 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
163 | June | 12 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
164 | June | 13 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
165 | June | 14 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
166 | June | 15 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
167 | June | 16 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
168 | June | 17 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
169 | June | 18 | 16 | 30720 | 5222.4 | 5013.504 | 10033591.5579 | 2787.1088 | 2226.3952 | 6000
170 | June | 19 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
171 | June | 20 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
172 | June | 21 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
173 | June | 22 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
174 | June | 23 | 16 | 30720 | 5222.4 | 5013.504 | 6646588.2545 | 1846.2745 | 3167.2295 | 6000
175 | June | 24 | 16 | 30720 | 5222.4 | 5013.504 | 12257989.5882 | 3404.9971 | 1608.5069 | 6000
176 | June | 25 | 16 | 30720 | 5222.4 | 5013.504 | 8571429.8312 | 2380.9527 | 2632.5513 | 6000
177 | June | 26 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
178 | June | 27 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
179 | June | 28 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
180 | June | 29 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
181 | June | 30 | 16 | 30720 | 5222.4 | 5013.504 | 3456000 | 960 | 4053.504 | 6000
182 | July | 1 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
183 | July | 2 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
184 | July | 3 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
185 | July | 4 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
186 | July | 5 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
187 | July | 6 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
188 | July | 7 | 15.75 | 30240 | 5140.8 | 4935.168 | 4785381.2883 | 1329.2726 | 3605.8954 | 6000
189 | July | 8 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
190 | July | 9 | 15.75 | 30240 | 5140.8 | 4935.168 | 6198442.0076 | 1721.7894 | 3213.3786 | 6000
191 | July | 10 | 15.75 | 30240 | 5140.8 | 4935.168 | 6432849.3732 | 1786.9026 | 3148.2654 | 6000
192 | July | 11 | 15.75 | 30240 | 5140.8 | 4935.168 | 7521813.3267 | 2089.3926 | 2845.7754 | 6000
193 | July | 12 | 15.75 | 30240 | 5140.8 | 4935.168 | 8571429.8312 | 2380.9527 | 2554.2153 | 6000
194 | July | 13 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
195 | July | 14 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
196 | July | 15 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
197 | July | 16 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
198 | July | 17 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
199 | July | 18 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
200 | July | 19 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
201 | July | 20 | 15.75 | 30240 | 5140.8 | 4935.168 | 5635364.2432 | 1565.379 | 3369.789 | 6000
202 | July | 21 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
203 | July | 22 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
204 | July | 23 | 15.75 | 30240 | 5140.8 | 4935.168 | 10594605.0666 | 2942.9459 | 1992.2221 | 6000
205 | July | 24 | 15.75 | 30240 | 5140.8 | 4935.168 | 8571429.8312 | 2380.9527 | 2554.2153 | 6000
206 | July | 25 | 15.75 | 30240 | 5140.8 | 4935.168 | 8684837.6853 | 2412.4549 | 2522.7131 | 6000
207 | July | 26 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
208 | July | 27 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
209 | July | 28 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
210 | July | 29 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
211 | July | 30 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
212 | July | 31 | 15.75 | 30240 | 5140.8 | 4935.168 | 3456000 | 960 | 3975.168 | 6000
213 | August | 1 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
214 | August | 2 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
215 | August | 3 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
216 | August | 4 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
217 | August | 5 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
218 | August | 6 | 14.2 | 27264 | 4634.88 | 4449.4848 | 8083231.7108 | 2245.3421 | 2204.1427 | 6000
219 | August | 7 | 14.2 | 27264 | 4634.88 | 4449.4848 | 12602806.9928 | 3500.7797 | 948.7051 | 6000
220 | August | 8 | 14.2 | 27264 | 4634.88 | 4449.4848 | 12714219.5618 | 3531.7277 | 917.7571 | 6000
221 | August | 9 | 14.2 | 27264 | 4634.88 | 4449.4848 | 7028411.395 | 1952.3365 | 2497.1483 | 6000
222 | August | 10 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
223 | August | 11 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
224 | August | 12 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
225 | August | 13 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
226 | August | 14 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
227 | August | 15 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
228 | August | 16 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
229 | August | 17 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
230 | August | 18 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
231 | August | 19 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
232 | August | 20 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
233 | August | 21 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
234 | August | 22 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
235 | August | 23 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
236 | August | 24 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
237 | August | 25 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
238 | August | 26 | 14.2 | 27264 | 4634.88 | 4449.4848 | 3456000 | 960 | 3489.4848 | 6000
239 | August | 27 | 14.2 | 27264 | 4634.88 | 4449.4848 | 7813618.2511 | 2170.4495 | 2279.0353 | 6000
240 | August | 28 | 14.2 | 27264 | 4634.88 | 4449.4848 | 11312535.7409 | 3142.371 | 1307.1138 | 6000
241 | August | 29 | 14.2 | 27264 | 4634.88 | 4449.4848 | 12714219.5618 | 3531.7277 | 917.7571 | 6000
242 | August | 30 | 14.2 | 27264 | 4634.88 | 4449.4848 | 12714219.5618 | 3531.7277 | 917.7571 | 6000
243 | August | 31 | 14.2 | 27264 | 4634.88 | 4449.4848 | 9593643.1427 | 2664.9009 | 1784.5839 | 6000
244 | September | 1 | 12.5 | 24000 | 4080 | 3916.8 | 12714219.5618 | 3531.7277 | 385.0723 | 6000
245 | September | 2 | 12.5 | 24000 | 4080 | 3916.8 | 5936504.9601 | 1649.0292 | 2267.7708 | 6000
246 | September | 3 | 12.5 | 24000 | 4080 | 3916.8 | 7521813.3267 | 2089.3926 | 1827.4074 | 6000
247 | September | 4 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
248 | September | 5 | 12.5 | 24000 | 4080 | 3916.8 | 6844090.3619 | 1901.1362 | 2015.6638 | 6000
249 | September | 6 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
250 | September | 7 | 12.5 | 24000 | 4080 | 3916.8 | 12714219.5618 | 3531.7277 | 385.0723 | 6000
251 | September | 8 | 12.5 | 24000 | 4080 | 3916.8 | 12139254.2976 | 3372.0151 | 544.7849 | 6000
252 | September | 9 | 12.5 | 24000 | 4080 | 3916.8 | 6646588.2545 | 1846.2745 | 2070.5255 | 6000
253 | September | 10 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
254 | September | 11 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
255 | September | 12 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
256 | September | 13 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
257 | September | 14 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
258 | September | 15 | 12.5 | 24000 | 4080 | 3916.8 | 7201762.0281 | 2000.4895 | 1916.3105 | 6000
259 | September | 16 | 12.5 | 24000 | 4080 | 3916.8 | 8571429.8312 | 2380.9527 | 1535.8473 | 6000
260 | September | 17 | 12.5 | 24000 | 4080 | 3916.8 | 7813618.2511 | 2170.4495 | 1746.3505 | 6000
261 | September | 18 | 12.5 | 24000 | 4080 | 3916.8 | 12714219.5618 | 3531.7277 | 385.0723 | 6000
262 | September | 19 | 12.5 | 24000 | 4080 | 3916.8 | 12714219.5618 | 3531.7277 | 385.0723 | 6000
263 | September | 20 | 12.5 | 24000 | 4080 | 3916.8 | 6646588.2545 | 1846.2745 | 2070.5255 | 6000
264 | September | 21 | 12.5 | 24000 | 4080 | 3916.8 | 8684837.6853 | 2412.4549 | 1504.3451 | 6000
265 | September | 22 | 12.5 | 24000 | 4080 | 3916.8 | 12714219.5618 | 3531.7277 | 385.0723 | 6000
266 | September | 23 | 12.5 | 24000 | 4080 | 3916.8 | 12714219.5618 | 3531.7277 | 385.0723 | 6000
267 | September | 24 | 12.5 | 24000 | 4080 | 3916.8 | 11770341.7991 | 3269.5394 | 647.2606 | 6000
268 | September | 25 | 12.5 | 24000 | 4080 | 3916.8 | 6844090.3619 | 1901.1362 | 2015.6638 | 6000
269 | September | 26 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
270 | September | 27 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
271 | September | 28 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
272 | September | 29 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
273 | September | 30 | 12.5 | 24000 | 4080 | 3916.8 | 3456000 | 960 | 2956.8 | 6000
274 | October | 1 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
275 | October | 2 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
276 | October | 3 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
277 | October | 4 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
278 | October | 5 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
279 | October | 6 | 10.75 | 20640 | 3508.8 | 3368.448 | 8571429.8312 | 2380.9527 | 987.4953 | 6000
280 | October | 7 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 6000
281 | October | 8 | 10.75 | 20640 | 3508.8 | 3368.448 | 10892071.6332 | 3025.5755 | 342.8725 | 5836.7203
282 | October | 9 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 6000
283 | October | 10 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 5836.7203
284 | October | 11 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 5673.4407
285 | October | 12 | 10.75 | 20640 | 3508.8 | 3368.448 | 5936504.9601 | 1649.0292 | 1719.4188 | 5510.161
286 | October | 13 | 10.75 | 20640 | 3508.8 | 3368.448 | 5635364.2432 | 1565.379 | 1803.069 | 6000
287 | October | 14 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
288 | October | 15 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
289 | October | 16 | 10.75 | 20640 | 3508.8 | 3368.448 | 12489682.1426 | 3469.3562 | -100.9082 | 6000
290 | October | 17 | 10.75 | 20640 | 3508.8 | 3368.448 | 9774154.5489 | 2715.0429 | 653.4051 | 5899.0918
291 | October | 18 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 6000
292 | October | 19 | 10.75 | 20640 | 3508.8 | 3368.448 | 5635364.2432 | 1565.379 | 1803.069 | 5836.7203
293 | October | 20 | 10.75 | 20640 | 3508.8 | 3368.448 | 11244401.369 | 3123.4448 | 245.0032 | 6000
294 | October | 21 | 10.75 | 20640 | 3508.8 | 3368.448 | 8571429.8312 | 2380.9527 | 987.4953 | 6000
295 | October | 22 | 10.75 | 20640 | 3508.8 | 3368.448 | 11105874.3094 | 3084.9651 | 283.4829 | 6000
296 | October | 23 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
297 | October | 24 | 10.75 | 20640 | 3508.8 | 3368.448 | 9500888.9292 | 2639.1358 | 729.3122 | 6000
298 | October | 25 | 10.75 | 20640 | 3508.8 | 3368.448 | 8571429.8312 | 2380.9527 | 987.4953 | 6000
299 | October | 26 | 10.75 | 20640 | 3508.8 | 3368.448 | 3456000 | 960 | 2408.448 | 6000
300 | October | 27 | 10.75 | 20640 | 3508.8 | 3368.448 | 9948529.8113 | 2763.4805 | 604.9675 | 6000
301 | October | 28 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 6000
302 | October | 29 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 5836.7203
303 | October | 30 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 5673.4407
304 | October | 31 | 10.75 | 20640 | 3508.8 | 3368.448 | 12714219.5618 | 3531.7277 | -163.2797 | 5510.161
305 | November | 1 | 9 | 17280 | 2937.6 | 2820.096 | 6432849.3732 | 1786.9026 | 1033.1934 | 5346.8814
306 | November | 2 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
307 | November | 3 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
308 | November | 4 | 9 | 17280 | 2937.6 | 2820.096 | 8211072.1918 | 2280.8534 | 539.2426 | 6000
309 | November | 5 | 9 | 17280 | 2937.6 | 2820.096 | 9593643.1427 | 2664.9009 | 155.1951 | 6000
310 | November | 6 | 9 | 17280 | 2937.6 | 2820.096 | 12714219.5618 | 3531.7277 | -711.6317 | 6000
311 | November | 7 | 9 | 17280 | 2937.6 | 2820.096 | 7365801.7526 | 2046.056 | 774.04 | 5288.3683
312 | November | 8 | 9 | 17280 | 2937.6 | 2820.096 | 6844090.3619 | 1901.1362 | 918.9598 | 6000
313 | November | 9 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
314 | November | 10 | 9 | 17280 | 2937.6 | 2820.096 | 12714219.5618 | 3531.7277 | -711.6317 | 6000
315 | November | 11 | 9 | 17280 | 2937.6 | 2820.096 | 12714219.5618 | 3531.7277 | -711.6317 | 5288.3683
316 | November | 12 | 9 | 17280 | 2937.6 | 2820.096 | 12714219.5618 | 3531.7277 | -711.6317 | 4576.7367
317 | November | 13 | 9 | 17280 | 2937.6 | 2820.096 | 11642767.8134 | 3234.1022 | -414.0062 | 3865.105
318 | November | 14 | 9 | 17280 | 2937.6 | 2820.096 | 5635364.2432 | 1565.379 | 1254.717 | 3451.0989
319 | November | 15 | 9 | 17280 | 2937.6 | 2820.096 | 9593643.1427 | 2664.9009 | 155.1951 | 4705.8159
320 | November | 16 | 9 | 17280 | 2937.6 | 2820.096 | 12714219.5618 | 3531.7277 | -711.6317 | 4861.011
321 | November | 17 | 9 | 17280 | 2937.6 | 2820.096 | 9684703.734 | 2690.1955 | 129.9005 | 4149.3794
322 | November | 18 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 4279.2799
323 | November | 19 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
324 | November | 20 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
325 | November | 21 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
326 | November | 22 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
327 | November | 23 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
328 | November | 24 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
329 | November | 25 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
330 | November | 26 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
331 | November | 27 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
332 | November | 28 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
333 | November | 29 | 9 | 17280 | 2937.6 | 2820.096 | 3456000 | 960 | 1860.096 | 6000
334 | November | 30 | 9 | 17280 | 2937.6 | 2820.096 | 12139254.2976 | 3372.0151 | -551.9191 | 6000
335 | December | 1 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 5448.0809
336 | December | 2 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 4501.4413
337 | December | 3 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 3554.8016
338 | December | 4 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 2608.1619
339 | December | 5 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 1661.5223
340 | December | 6 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 714.8826
341 | December | 7 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 0 | 1
342 | December | 8 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 0 | 1
343 | December | 9 | 8.25 | 15840 | 2692.8 | 2585.088 | 9008199.5737 | 2502.2777 | 82.8103 | 0 | 1
344 | December | 10 | 8.25 | 15840 | 2692.8 | 2585.088 | 11895536.0973 | 3304.3156 | -719.2276 | 82.8103
345 | December | 11 | 8.25 | 15840 | 2692.8 | 2585.088 | 8211072.1918 | 2280.8534 | 304.2346 | 0 | 1
346 | December | 12 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 304.2346
347 | December | 13 | 8.25 | 15840 | 2692.8 | 2585.088 | 3456000 | 960 | 1625.088 | 0 | 1
348 | December | 14 | 8.25 | 15840 | 2692.8 | 2585.088 | 7521813.3267 | 2089.3926 | 495.6954 | 1625.088
349 | December | 15 | 8.25 | 15840 | 2692.8 | 2585.088 | 7950904.5817 | 2208.5846 | 376.5034 | 2120.7834
350 | December | 16 | 8.25 | 15840 | 2692.8 | 2585.088 | 7365801.7526 | 2046.056 | 539.032 | 2497.2868
351 | December | 17 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 3036.3188
352 | December | 18 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 2089.6791
353 | December | 19 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 1143.0394
354 | December | 20 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 196.3998
355 | December | 21 | 8.25 | 15840 | 2692.8 | 2585.088 | 10819093.7566 | 3005.3038 | -420.2158 | 0 | 1
356 | December | 22 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 0 | 1
357 | December | 23 | 8.25 | 15840 | 2692.8 | 2585.088 | 10964175.5379 | 3045.6043 | -460.5163 | 0 | 1
358 | December | 24 | 8.25 | 15840 | 2692.8 | 2585.088 | 3456000 | 960 | 1625.088 | 0 | 1
359 | December | 25 | 8.25 | 15840 | 2692.8 | 2585.088 | 3456000 | 960 | 1625.088 | 1625.088
360 | December | 26 | 8.25 | 15840 | 2692.8 | 2585.088 | 12714219.5618 | 3531.7277 | -946.6397 | 3250.176
361 | December | 27 | 8.25 | 15840 | 2692.8 | 2585.088 | 6844090.3619 | 1901.1362 | 683.9518 | 2303.5363
362 | December | 28 | 8.25 | 15840 | 2692.8 | 2585.088 | 4785381.2883 | 1329.2726 | 1255.8154 | 2987.4881
363 | December | 29 | 8.25 | 15840 | 2692.8 | 2585.088 | 3456000 | 960 | 1625.088 | 4243.3036
364 | December | 30 | 8.25 | 15840 | 2692.8 | 2585.088 | 3456000 | 960 | 1625.088 | 5868.3916
365 | December | 31 | 8.25 | 15840 | 2692.8 | 2585.088 | 3456000 | 960 | 1625.088 | 6000

## On Demand Flow Calcs
Storage Tank Height | h | 20 | m
Distance to Storage Tank | L | 63.4429 | m
Pipe diameter | D | 0.02 | m |  |  | Measured Cf | 15040 | Filter | Up
Pipe area | A | 0.00031416 | m^2
Pipe friction factor | f | 0.05
Loss coefficient | K | 12
Pressure from storage | rho g h | 196200 | Pa
Consumption | C | 432 | L/day
|  | Cf | Actual Filter | Filter Life Data [L]
Filter Size | Present? | [Pa/(m/s)] | Life [L] | Non pre-filter | 5 micron pre | 200 micron pre |  | Quadratic Equation Solver
1 micron | y | 2511.68 | 20000 | 5000 | 20000 | 15000 |  | A | 85303.6096
5 micron | y | 1252.832 | 20000 | 10000 | 0 | 20000 |  | B | 0
200 micron | y | 62.7168 | 20000 | 20000 | 0 | 0 |  | C | -196200
=IF('InputOutputData'!E36="Data 1( |  | 3827.2288
[8 empty] | v1 | 1.5166 | m/s
[8 empty] | v2 | -1.5166 | m/s
[8 empty] | v | 1.5166 | m/s | v=1.5 m/s
[8 empty] | Q | 28.5869 | L/min | Q=28.6 L/min
v | Q | Pressure Loss | Storage Pressure
[m/s] | [L/min] | [Pa] | [Pa]
0 | 0 | 0 | 196200
0.05 | 0.94248 | 213.259 | 196200
0.1 | 1.885 | 853.0361 | 196200
0.15 | 2.8274 | 1919.3312 | 196200
0.2 | 3.7699 | 3412.1444 | 196200
0.25 | 4.7124 | 5331.4756 | 196200
0.3 | 5.6549 | 7677.3249 | 196200
0.35 | 6.5973 | 10449.6922 | 196200
0.4 | 7.5398 | 13648.5775 | 196200
0.45 | 8.4823 | 17273.9809 | 196200
0.5 | 9.4248 | 21325.9024 | 196200
0.55 | 10.3673 | 25804.3419 | 196200
0.6 | 11.3097 | 30709.2995 | 196200
0.65 | 12.2522 | 36040.7751 | 196200
0.7 | 13.1947 | 41798.7687 | 196200
0.75 | 14.1372 | 47983.2804 | 196200
0.8 | 15.0796 | 54594.3102 | 196200
0.85 | 16.0221 | 61631.858 | 196200
0.9 | 16.9646 | 69095.9238 | 196200
0.95 | 17.9071 | 76986.5077 | 196200
1 | 18.8496 | 85303.6096 | 196200
1.05 | 19.792 | 94047.2296 | 196200
1.1 | 20.7345 | 103217.3676 | 196200
1.15 | 21.677 | 112814.0237 | 196200
1.2 | 22.6195 | 122837.1979 | 196200
1.25 | 23.5619 | 133286.89 | 196200
1.3 | 24.5044 | 144163.1003 | 196200
1.35 | 25.4469 | 155465.8285 | 196200
1.4 | 26.3894 | 167195.0749 | 196200
1.45 | 27.3319 | 179350.8392 | 196200
1.5 | 28.2743 | 191933.1217 | 196200
1.55 | 29.2168 | 204941.9221 | 196200
1.6 | 30.1593 | 218377.2406 | 196200
1.65 | 31.1018 | 232239.0772 | 196200
1.7 | 32.0442 | 246527.4318 | 196200
1.75 | 32.9867 | 261242.3045 | 196200
1.8 | 33.9292 | 276383.6952 | 196200
1.85 | 34.8717 | 291951.604 | 196200
1.9 | 35.8142 | 307946.0308 | 196200
1.95 | 36.7566 | 324366.9756 | 196200
2 | 37.6991 | 341214.4385 | 196200
2.05 | 38.6416 | 358488.4195 | 196200
2.1 | 39.5841 | 376188.9185 | 196200
2.15 | 40.5265 | 394315.9355 | 196200
2.2 | 41.469 | 412869.4706 | 196200
2.25 | 42.4115 | 431849.5237 | 196200
2.3 | 43.354 | 451256.0949 | 196200
2.35 | 44.2965 | 471089.1842 | 196200
2.4 | 45.2389 | 491348.7915 | 196200
2.45 | 46.1814 | 512034.9168 | 196200
2.5 | 47.1239 | 533147.5602 | 196200
2.55 | 48.0664 | 554686.7216 | 196200
2.6 | 49.0088 | 576652.4011 | 196200
2.65 | 49.9513 | 599044.5986 | 196200

## E + U + G satisfaction
Chlorine Health Severity | 4 | [ ] |  | Chlorine risk exposure period | 52.1429 | [days] |  | Emin | 1 | [ ] |  | Disinfection | Chlorine
Chlorine Environment Severity | 3 | [ ] |  | Diesel risk exposure period | 0 | [days] |  | Emax | 32 | [ ] |  | Energy | Solar
Diesel Health Severity | 2 | [ ]
Diesel Environment Severity | 3 | [ ]
Chlorine Risk Likelihood Rating | Diesel Risk Likehood Rating |  |  | Chlorine Overall Risk | Diesal Overall Risk | Overall Risk | Risk Satisfaction (%)
2.023 | #NUM! |  |  | 14.161 | 0 | 14.161 | 61.741
Land Use | 0.10862 | Volume Catchment Tank | 1.5 | m^3
|  | Volume Storage | 36 | m^3
|  | Distance to house | 60.208 | m
|  | Height | 0 | m
|  | AC area | 0 | m^2
|  | AC distance | N/A | m
Relative GHG | 69.1926 |  | Consumption | 432
|  | Relative System |  |  |  | Our System
|  | Total Consumption | 788400 | L |  | Energy? | Solar
|  | Centralized Water Treatment | 78.84 | kgCO2e |  | Solar Panel | HES-260 | 1984 | kgCO2e | Quantity | 4
|  | Land and Sea Transport | 5045.76 | kgCO2e |  | Battery | 3 | 720 | kgCO2e
|  | Storage and Distribution | 2408 | kgCO2e |  | Inverter | Yes | 100 | kgCO2e
|  | Total | 7532.6 | kgCO2e |  | Diesel | no | 0 | kgCO2e
[6 empty] | Diesel Fuel | 910.4885 | 0 | kgCO2e
[6 empty] | Storage and Distribution |  | 2408 | kgCO2e
[6 empty] | Total |  | 5212 | kgCO2e
Note on F1: Rohin Dhaliwal: to be replaced with calculated values later

## Maintenance Calculations
Storage Tank Height | h | 20 | m
Distance to Storage Tank | L | 63.9316 | m | [6 empty] | Disinfection | Chlorine
Pipe diameter | D | 0.02 | m | [6 empty] | Energy | Solar
Pipe area | A | 0.00031416 | m^2
Pipe friction factor | f | 0.05
Loss coefficient | K | 8
Pressure from storage | rho g h | 196200 | Pa |  |  |  |  | Maintenance
Consumption | C | 432 | L/day |  |  |  |  | Filters | 7
[8 empty] | Ozone or Chlorine | 7
[8 empty] | UV | 1
[8 empty] | Pump | 1
|  | Cf | Actual Filter | Filter Life Data [L] |  |  |  | Solar or Diesel | 4
Filter Size | Present? | [Pa/(m/s)] | Life [L] | Non pre-filter | 5 micron pre | 200 micron pre |  | Generator | 0
1 micron | y | 2511.68 | 20000 | 5000 | 20000 | 15000 |  | Total Maintenance | 20
5 micron | y | 1252.832 | 20000 | 10000 |  | 20000
200 micron | y | 62.7168 | 20000 | 20000
Total |  | 3827.2288
System Performance |  |  |  | Total Filter Changes
M | 7 | #/year |  | 1 micron | 5 micron | 200 micron
S(M) | 81.1745 |  |  | 7 | 7 | 7
| Total Volume Through Filter [L] |  |  | Maintenance for Filter Change |  |  | Operation
Day | 1 micron | 5 micron | 200 micron | 1 micron | 5 micron | 200 micron
1 | 432 | 432 | 432
2 | 864 | 864 | 864
3 | 1296 | 1296 | 1296
4 | 1728 | 1728 | 1728
5 | 2160 | 2160 | 2160
6 | 2592 | 2592 | 2592
7 | 3024 | 3024 | 3024
8 | 3456 | 3456 | 3456
9 | 3888 | 3888 | 3888
10 | 4320 | 4320 | 4320
11 | 4752 | 4752 | 4752
12 | 5184 | 5184 | 5184
13 | 5616 | 5616 | 5616
14 | 6048 | 6048 | 6048
15 | 6480 | 6480 | 6480
16 | 6912 | 6912 | 6912
17 | 7344 | 7344 | 7344
18 | 7776 | 7776 | 7776
19 | 8208 | 8208 | 8208
20 | 8640 | 8640 | 8640
21 | 9072 | 9072 | 9072
22 | 9504 | 9504 | 9504
23 | 9936 | 9936 | 9936
24 | 10368 | 10368 | 10368
25 | 10800 | 10800 | 10800
26 | 11232 | 11232 | 11232
27 | 11664 | 11664 | 11664
28 | 12096 | 12096 | 12096
29 | 12528 | 12528 | 12528
30 | 12960 | 12960 | 12960
31 | 13392 | 13392 | 13392
32 | 13824 | 13824 | 13824
33 | 14256 | 14256 | 14256
34 | 14688 | 14688 | 14688
35 | 15120 | 15120 | 15120
36 | 15552 | 15552 | 15552
37 | 15984 | 15984 | 15984
38 | 16416 | 16416 | 16416
39 | 16848 | 16848 | 16848
40 | 17280 | 17280 | 17280
41 | 17712 | 17712 | 17712
42 | 18144 | 18144 | 18144
43 | 18576 | 18576 | 18576
44 | 19008 | 19008 | 19008
45 | 19440 | 19440 | 19440
46 | 19872 | 19872 | 19872
47 | 432 | 432 | 432 | 1 | 1 | 1 | 1
48 | 864 | 864 | 864
49 | 1296 | 1296 | 1296
50 | 1728 | 1728 | 1728
51 | 2160 | 2160 | 2160
52 | 2592 | 2592 | 2592
53 | 3024 | 3024 | 3024
54 | 3456 | 3456 | 3456
55 | 3888 | 3888 | 3888
56 | 4320 | 4320 | 4320
57 | 4752 | 4752 | 4752
58 | 5184 | 5184 | 5184
59 | 5616 | 5616 | 5616
60 | 6048 | 6048 | 6048
61 | 6480 | 6480 | 6480
62 | 6912 | 6912 | 6912
63 | 7344 | 7344 | 7344
64 | 7776 | 7776 | 7776
65 | 8208 | 8208 | 8208
66 | 8640 | 8640 | 8640
67 | 9072 | 9072 | 9072
68 | 9504 | 9504 | 9504
69 | 9936 | 9936 | 9936
70 | 10368 | 10368 | 10368
71 | 10800 | 10800 | 10800
72 | 11232 | 11232 | 11232
73 | 11664 | 11664 | 11664
74 | 12096 | 12096 | 12096
75 | 12528 | 12528 | 12528
76 | 12960 | 12960 | 12960
77 | 13392 | 13392 | 13392
78 | 13824 | 13824 | 13824
79 | 14256 | 14256 | 14256
80 | 14688 | 14688 | 14688
81 | 15120 | 15120 | 15120
82 | 15552 | 15552 | 15552
83 | 15984 | 15984 | 15984
84 | 16416 | 16416 | 16416
85 | 16848 | 16848 | 16848
86 | 17280 | 17280 | 17280
87 | 17712 | 17712 | 17712
88 | 18144 | 18144 | 18144
89 | 18576 | 18576 | 18576
90 | 19008 | 19008 | 19008
91 | 19440 | 19440 | 19440
92 | 19872 | 19872 | 19872
93 | 432 | 432 | 432 | 1 | 1 | 1 | 1
94 | 864 | 864 | 864
95 | 1296 | 1296 | 1296
96 | 1728 | 1728 | 1728
97 | 2160 | 2160 | 2160
98 | 2592 | 2592 | 2592
99 | 3024 | 3024 | 3024
100 | 3456 | 3456 | 3456
101 | 3888 | 3888 | 3888
102 | 4320 | 4320 | 4320
103 | 4752 | 4752 | 4752
104 | 5184 | 5184 | 5184
105 | 5616 | 5616 | 5616
106 | 6048 | 6048 | 6048
107 | 6480 | 6480 | 6480
108 | 6912 | 6912 | 6912
109 | 7344 | 7344 | 7344
110 | 7776 | 7776 | 7776
111 | 8208 | 8208 | 8208
112 | 8640 | 8640 | 8640
113 | 9072 | 9072 | 9072
114 | 9504 | 9504 | 9504
115 | 9936 | 9936 | 9936
116 | 10368 | 10368 | 10368
117 | 10800 | 10800 | 10800
118 | 11232 | 11232 | 11232
119 | 11664 | 11664 | 11664
120 | 12096 | 12096 | 12096
121 | 12528 | 12528 | 12528
122 | 12960 | 12960 | 12960
123 | 13392 | 13392 | 13392
124 | 13824 | 13824 | 13824
125 | 14256 | 14256 | 14256
126 | 14688 | 14688 | 14688
127 | 15120 | 15120 | 15120
128 | 15552 | 15552 | 15552
129 | 15984 | 15984 | 15984
130 | 16416 | 16416 | 16416
131 | 16848 | 16848 | 16848
132 | 17280 | 17280 | 17280
133 | 17712 | 17712 | 17712
134 | 18144 | 18144 | 18144
135 | 18576 | 18576 | 18576
136 | 19008 | 19008 | 19008
137 | 19440 | 19440 | 19440
138 | 19872 | 19872 | 19872
139 | 432 | 432 | 432 | 1 | 1 | 1 | 1
140 | 864 | 864 | 864
141 | 1296 | 1296 | 1296
142 | 1728 | 1728 | 1728
143 | 2160 | 2160 | 2160
144 | 2592 | 2592 | 2592
145 | 3024 | 3024 | 3024
146 | 3456 | 3456 | 3456
147 | 3888 | 3888 | 3888
148 | 4320 | 4320 | 4320
149 | 4752 | 4752 | 4752
150 | 5184 | 5184 | 5184
151 | 5616 | 5616 | 5616
152 | 6048 | 6048 | 6048
153 | 6480 | 6480 | 6480
154 | 6912 | 6912 | 6912
155 | 7344 | 7344 | 7344
156 | 7776 | 7776 | 7776
157 | 8208 | 8208 | 8208
158 | 8640 | 8640 | 8640
159 | 9072 | 9072 | 9072
160 | 9504 | 9504 | 9504
161 | 9936 | 9936 | 9936
162 | 10368 | 10368 | 10368
163 | 10800 | 10800 | 10800
164 | 11232 | 11232 | 11232
165 | 11664 | 11664 | 11664
166 | 12096 | 12096 | 12096
167 | 12528 | 12528 | 12528
168 | 12960 | 12960 | 12960
169 | 13392 | 13392 | 13392
170 | 13824 | 13824 | 13824
171 | 14256 | 14256 | 14256
172 | 14688 | 14688 | 14688
173 | 15120 | 15120 | 15120
174 | 15552 | 15552 | 15552
175 | 15984 | 15984 | 15984
176 | 16416 | 16416 | 16416
177 | 16848 | 16848 | 16848
178 | 17280 | 17280 | 17280
179 | 17712 | 17712 | 17712
180 | 18144 | 18144 | 18144
181 | 18576 | 18576 | 18576
182 | 19008 | 19008 | 19008
183 | 19440 | 19440 | 19440
184 | 19872 | 19872 | 19872
185 | 432 | 432 | 432 | 1 | 1 | 1 | 1
186 | 864 | 864 | 864
187 | 1296 | 1296 | 1296
188 | 1728 | 1728 | 1728
189 | 2160 | 2160 | 2160
190 | 2592 | 2592 | 2592
191 | 3024 | 3024 | 3024
192 | 3456 | 3456 | 3456
193 | 3888 | 3888 | 3888
194 | 4320 | 4320 | 4320
195 | 4752 | 4752 | 4752
196 | 5184 | 5184 | 5184
197 | 5616 | 5616 | 5616
198 | 6048 | 6048 | 6048
199 | 6480 | 6480 | 6480
200 | 6912 | 6912 | 6912
201 | 7344 | 7344 | 7344
202 | 7776 | 7776 | 7776
203 | 8208 | 8208 | 8208
204 | 8640 | 8640 | 8640
205 | 9072 | 9072 | 9072
206 | 9504 | 9504 | 9504
207 | 9936 | 9936 | 9936
208 | 10368 | 10368 | 10368
209 | 10800 | 10800 | 10800
210 | 11232 | 11232 | 11232
211 | 11664 | 11664 | 11664
212 | 12096 | 12096 | 12096
213 | 12528 | 12528 | 12528
214 | 12960 | 12960 | 12960
215 | 13392 | 13392 | 13392
216 | 13824 | 13824 | 13824
217 | 14256 | 14256 | 14256
218 | 14688 | 14688 | 14688
219 | 15120 | 15120 | 15120
220 | 15552 | 15552 | 15552
221 | 15984 | 15984 | 15984
222 | 16416 | 16416 | 16416
223 | 16848 | 16848 | 16848
224 | 17280 | 17280 | 17280
225 | 17712 | 17712 | 17712
226 | 18144 | 18144 | 18144
227 | 18576 | 18576 | 18576
228 | 19008 | 19008 | 19008
229 | 19440 | 19440 | 19440
230 | 19872 | 19872 | 19872
231 | 432 | 432 | 432 | 1 | 1 | 1 | 1
232 | 864 | 864 | 864
233 | 1296 | 1296 | 1296
234 | 1728 | 1728 | 1728
235 | 2160 | 2160 | 2160
236 | 2592 | 2592 | 2592
237 | 3024 | 3024 | 3024
238 | 3456 | 3456 | 3456
239 | 3888 | 3888 | 3888
240 | 4320 | 4320 | 4320
241 | 4752 | 4752 | 4752
242 | 5184 | 5184 | 5184
243 | 5616 | 5616 | 5616
244 | 6048 | 6048 | 6048
245 | 6480 | 6480 | 6480
246 | 6912 | 6912 | 6912
247 | 7344 | 7344 | 7344
248 | 7776 | 7776 | 7776
249 | 8208 | 8208 | 8208
250 | 8640 | 8640 | 8640
251 | 9072 | 9072 | 9072
252 | 9504 | 9504 | 9504
253 | 9936 | 9936 | 9936
254 | 10368 | 10368 | 10368
255 | 10800 | 10800 | 10800
256 | 11232 | 11232 | 11232
257 | 11664 | 11664 | 11664
258 | 12096 | 12096 | 12096
259 | 12528 | 12528 | 12528
260 | 12960 | 12960 | 12960
261 | 13392 | 13392 | 13392
262 | 13824 | 13824 | 13824
263 | 14256 | 14256 | 14256
264 | 14688 | 14688 | 14688
265 | 15120 | 15120 | 15120
266 | 15552 | 15552 | 15552
267 | 15984 | 15984 | 15984
268 | 16416 | 16416 | 16416
269 | 16848 | 16848 | 16848
270 | 17280 | 17280 | 17280
271 | 17712 | 17712 | 17712
272 | 18144 | 18144 | 18144
273 | 18576 | 18576 | 18576
274 | 19008 | 19008 | 19008
275 | 19440 | 19440 | 19440
276 | 19872 | 19872 | 19872
277 | 432 | 432 | 432 | 1 | 1 | 1 | 1
278 | 864 | 864 | 864
279 | 1296 | 1296 | 1296
280 | 1728 | 1728 | 1728
281 | 2160 | 2160 | 2160
282 | 2592 | 2592 | 2592
283 | 3024 | 3024 | 3024
284 | 3456 | 3456 | 3456
285 | 3888 | 3888 | 3888
286 | 4320 | 4320 | 4320
287 | 4752 | 4752 | 4752
288 | 5184 | 5184 | 5184
289 | 5616 | 5616 | 5616
290 | 6048 | 6048 | 6048
291 | 6480 | 6480 | 6480
292 | 6912 | 6912 | 6912
293 | 7344 | 7344 | 7344
294 | 7776 | 7776 | 7776
295 | 8208 | 8208 | 8208
296 | 8640 | 8640 | 8640
297 | 9072 | 9072 | 9072
298 | 9504 | 9504 | 9504
299 | 9936 | 9936 | 9936
300 | 10368 | 10368 | 10368
301 | 10800 | 10800 | 10800
302 | 11232 | 11232 | 11232
303 | 11664 | 11664 | 11664
304 | 12096 | 12096 | 12096
305 | 12528 | 12528 | 12528
306 | 12960 | 12960 | 12960
307 | 13392 | 13392 | 13392
308 | 13824 | 13824 | 13824
309 | 14256 | 14256 | 14256
310 | 14688 | 14688 | 14688
311 | 15120 | 15120 | 15120
312 | 15552 | 15552 | 15552
313 | 15984 | 15984 | 15984
314 | 16416 | 16416 | 16416
315 | 16848 | 16848 | 16848
316 | 17280 | 17280 | 17280
317 | 17712 | 17712 | 17712
318 | 18144 | 18144 | 18144
319 | 18576 | 18576 | 18576
320 | 19008 | 19008 | 19008
321 | 19440 | 19440 | 19440
322 | 19872 | 19872 | 19872
323 | 432 | 432 | 432 | 1 | 1 | 1 | 1
324 | 864 | 864 | 864
325 | 1296 | 1296 | 1296
326 | 1728 | 1728 | 1728
327 | 2160 | 2160 | 2160
328 | 2592 | 2592 | 2592
329 | 3024 | 3024 | 3024
330 | 3456 | 3456 | 3456
331 | 3888 | 3888 | 3888
332 | 4320 | 4320 | 4320
333 | 4752 | 4752 | 4752
334 | 5184 | 5184 | 5184
335 | 5616 | 5616 | 5616
336 | 6048 | 6048 | 6048
337 | 6480 | 6480 | 6480
338 | 6912 | 6912 | 6912
339 | 7344 | 7344 | 7344
340 | 7776 | 7776 | 7776
341 | 8208 | 8208 | 8208
342 | 8640 | 8640 | 8640
343 | 9072 | 9072 | 9072
344 | 9504 | 9504 | 9504
345 | 9936 | 9936 | 9936
346 | 10368 | 10368 | 10368
347 | 10800 | 10800 | 10800
348 | 11232 | 11232 | 11232
349 | 11664 | 11664 | 11664
350 | 12096 | 12096 | 12096
351 | 12528 | 12528 | 12528
352 | 12960 | 12960 | 12960
353 | 13392 | 13392 | 13392
354 | 13824 | 13824 | 13824
355 | 14256 | 14256 | 14256
356 | 14688 | 14688 | 14688
357 | 15120 | 15120 | 15120
358 | 15552 | 15552 | 15552
359 | 15984 | 15984 | 15984
360 | 16416 | 16416 | 16416
361 | 16848 | 16848 | 16848
362 | 17280 | 17280 | 17280
363 | 17712 | 17712 | 17712
364 | 18144 | 18144 | 18144

## More accurate Energy (diesel)
|  | Parameters | [5 empty] | Pump Chosen | Pump C | Pump |  |  |  | Battery |  |  |  |  | Density | 1000 | [kg/m^3]
|  | Daily Consumption |  | 432 | L/Day |  |  |  |  | Pressure | 336.5716 | kPa |  | # of Batteries |  | 1 |  |  | Gravity | 9.81 | [m/s^2]
|  | Catchment Area |  | 100 | m^2 |  |  |  |  | Qmax | 136.5 | LPM |  | Capacity |  | 2000 | Wh
|  | Collection Volume |  | 1.5 | m^3 |  |  |  |  | Efficiency | 70 | % |  | Effiecency |  | 96 | % |  | Heating Value Diesel | 40 | [MJ/L]
|  | Storage Volume |  | 36 | m^3 | [13 empty] | Efficiency of Generator | 35% | [ ]
|  | Distance |  | 63.9316 | m |  |  |  |  | Contact Time | 10 | [min] |  | UV Lamp Size | 40 | [W]
|  | Elavation Of Base |  | 21.5 | m |  |  |  |  | CT_Ozone | 50 | [mg min/L] | [6 empty] | Pump Cont.
|  | Usage Day |  | 31 | [5 empty] | Energy for O3 | 2 | [MJ / g] | [6 empty] | A | 0.72
[19 empty] | B | 0.55
Daily Rainfall | Qin | Qin | Day | Vstorage | M energy | Effiency | E_energy | g_Ozone | E_Energy Ozone | E_Batt UV | E_Energy Diesel | E_total | Fuel | Without Water |  | Fuel Total | 182.0977 | L | 183
[mm] | [LPM] | [m^3 / day] |  | [m^3] | [J] | [%] | [J] | [g] | [J] | [J] | [J] | [J] | [L]
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7.8 | 0.54167 | 0.78 | 1 | 0.78 | 262525.8416 | 0.041325 | 6352644.4742 | 3.9 | 7800000 | 3456000 | 3750000 | 10102644.4742 | 0.72162 |  |  |  | 94.7917
1 | 0.069444 | 0.1 | 2 | 0.88 | 33657.1592 | 0.01334 | 2523046.647 | 0.5 | 1000000 | 3456000 | 3750000 | 6273046.647 | 0.44807
13.4 | 0.93056 | 1.34 | 3 | 2.22 | 451005.9329 | 0.055695 | 8097830.4211 | 6.7 | 13400000 | 3456000 | 3750000 | 11847830.4211 | 0.84627
64.2 | 1.0417 | 1.5 | 4 | 3.72 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625 |  |  | Days Without Water | 10
32.2 | 1.0417 | 1.5 | 5 | 5.22 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625 |  |  | Reliability | 355
2.8 | 0.19444 | 0.28 | 6 | 5.5 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421
0 | 0 | 0 | 7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 8 | 5.5 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.8 | 0.055556 | 0.08 | 9 | 5.58 | 26925.7273 | 0.011799 | 2282064.5633 | 0.4 | 800000 | 3456000 | 3750000 | 6032064.5633 | 0.43086
0 | 0 | 0 | 10 | 5.58 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 11 | 5.58 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 12 | 5.58 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 13 | 5.58 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.4 | 0.027778 | 0.04 | 14 | 5.62 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
35.4 | 1.0417 | 1.5 | 15 | 7.12 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
6 | 0.41667 | 0.6 | 16 | 7.72 | 201942.955 | 0.035763 | 5646631.6913 | 3 | 6000000 | 3456000 | 3750000 | 9396631.6913 | 0.67119
20.4 | 1.0417 | 1.5 | 17 | 9.22 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
16.6 | 1.0417 | 1.5 | 18 | 10.72 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
2.6 | 0.18056 | 0.26 | 19 | 10.98 | 87508.6139 | 0.022568 | 3877627.2231 | 1.3 | 2600000 | 3456000 | 3750000 | 7627627.2231 | 0.54483
0.4 | 0.027778 | 0.04 | 20 | 11.02 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
18.4 | 1.0417 | 1.5 | 21 | 12.52 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
14 | 0.97222 | 1.4 | 22 | 13.92 | 471200.2284 | 0.057058 | 8258338.0055 | 7 | 14000000 | 3456000 | 3750000 | 12008338.0055 | 0.85774
90.8 | 1.0417 | 1.5 | 23 | 15.42 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
40 | 1.0417 | 1.5 | 24 | 16.92 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
1.8 | 0.125 | 0.18 | 25 | 17.1 | 60582.8865 | 0.018433 | 3286618.4834 | 0.9 | 1800000 | 3456000 | 3750000 | 7036618.4834 | 0.50262
2.8 | 0.19444 | 0.28 | 26 | 17.38 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421
2.8 | 0.19444 | 0.28 | 27 | 17.66 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421
0 | 0 | 0 | 28 | 17.66 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 29 | 17.66 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.6 | 0.041667 | 0.06 | 30 | 17.72 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
5.8 | 0.40278 | 0.58 | 31 | 18.3 | 195211.5232 | 0.035102 | 5561297.8149 | 2.9 | 5800000 | 3456000 | 3750000 | 9311297.8149 | 0.66509
8 | 0.55556 | 0.8 | 32 | 18.668 | 269257.2734 | 0.041906 | 6425254.2184 | 4 | 8000000 | 3456000 | 3750000 | 10175254.2184 | 0.7268
27 | 1.0417 | 1.5 | 33 | 19.736 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.6 | 0.041667 | 0.06 | 34 | 19.364 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
36 | 1.0417 | 1.5 | 35 | 20.432 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
27.2 | 1.0417 | 1.5 | 36 | 21.5 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
28.2 | 1.0417 | 1.5 | 37 | 22.568 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
39.2 | 1.0417 | 1.5 | 38 | 23.636 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
6.6 | 0.45833 | 0.66 | 39 | 23.864 | 222137.2506 | 0.037691 | 5893586.9827 | 3.3 | 6600000 | 3456000 | 3750000 | 9643586.9827 | 0.68883
3.2 | 0.22222 | 0.32 | 40 | 23.752 | 107702.9094 | 0.0253 | 4257053.1739 | 1.6 | 3200000 | 3456000 | 3750000 | 8007053.1739 | 0.57193
0.2 | 0.013889 | 0.02 | 41 | 23.34 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
19.6 | 1.0417 | 1.5 | 42 | 24.408 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
30.4 | 1.0417 | 1.5 | 43 | 25.476 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
19 | 1.0417 | 1.5 | 44 | 26.544 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.2 | 0.013889 | 0.02 | 45 | 26.132 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
0 | 0 | 0 | 46 | 25.7 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 47 | 25.268 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 48 | 24.836 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
4 | 0.27778 | 0.4 | 49 | 24.804 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
11 | 0.76389 | 1.1 | 50 | 25.472 | 370228.7509 | 0.049949 | 7412149.0722 | 5.5 | 11000000 | 3456000 | 3750000 | 11162149.0722 | 0.7973
0.4 | 0.027778 | 0.04 | 51 | 25.08 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
0 | 0 | 0 | 52 | 24.648 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 53 | 24.216 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 54 | 23.784 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.2 | 0.013889 | 0.02 | 55 | 23.372 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
4.6 | 0.31944 | 0.46 | 56 | 23.4 | 154822.9322 | 0.030895 | 5011266.7336 | 2.3 | 4600000 | 3456000 | 3750000 | 8761266.7336 | 0.6258
8.8 | 0.61111 | 0.88 | 57 | 23.848 | 296183.0007 | 0.044166 | 6706074.7466 | 4.4 | 8800000 | 3456000 | 3750000 | 10456074.7466 | 0.74686
0.4 | 0.027778 | 0.04 | 58 | 23.456 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
0 | 0 | 0 | 59 | 23.024 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
1.2 | 0.083333 | 0.12 | 60 | 22.712 | 40388.591 | 0.014747 | 2738701.4233 | 0.6 | 1200000 | 3456000 | 3750000 | 6488701.4233 | 0.46348
0 | 0 | 0 | 61 | 22.28 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 62 | 21.848 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.4 | 0.027778 | 0.04 | 63 | 21.456 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
1.8 | 0.125 | 0.18 | 64 | 21.204 | 60582.8865 | 0.018433 | 3286618.4834 | 0.9 | 1800000 | 3456000 | 3750000 | 7036618.4834 | 0.50262
0.8 | 0.055556 | 0.08 | 65 | 20.852 | 26925.7273 | 0.011799 | 2282064.5633 | 0.4 | 800000 | 3456000 | 3750000 | 6032064.5633 | 0.43086
0 | 0 | 0 | 66 | 20.42 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.4 | 0.027778 | 0.04 | 67 | 20.028 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
0.4 | 0.027778 | 0.04 | 68 | 19.636 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
2.8 | 0.19444 | 0.28 | 69 | 19.484 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421
13.6 | 0.94444 | 1.36 | 70 | 20.412 | 457737.3648 | 0.056152 | 8151769.053 | 6.8 | 13600000 | 3456000 | 3750000 | 11901769.053 | 0.85013
8.6 | 0.59722 | 0.86 | 71 | 20.84 | 289451.5689 | 0.04361 | 6637241.9437 | 4.3 | 8600000 | 3456000 | 3750000 | 10387241.9437 | 0.74195
17.4 | 1.0417 | 1.5 | 72 | 21.908 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.6 | 0.041667 | 0.06 | 73 | 21.536 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
0 | 0 | 0 | 74 | 21.104 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 75 | 20.672 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 76 | 20.24 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
31 | 1.0417 | 1.5 | 77 | 21.308 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
35.4 | 1.0417 | 1.5 | 78 | 22.376 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
28.6 | 1.0417 | 1.5 | 79 | 23.444 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0 | 0 | 0 | 80 | 23.012 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
7 | 0.48611 | 0.7 | 81 | 23.28 | 235600.1142 | 0.038933 | 6051384.2332 | 3.5 | 7000000 | 3456000 | 3750000 | 9801384.2332 | 0.7001
9.6 | 0.66667 | 0.96 | 82 | 23.808 | 323108.7281 | 0.046337 | 6973079.3422 | 4.8 | 9600000 | 3456000 | 3750000 | 10723079.3422 | 0.76593
18.2 | 1.0417 | 1.5 | 83 | 24.876 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
104.4 | 1.0417 | 1.5 | 84 | 25.944 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
33.2 | 1.0417 | 1.5 | 85 | 27.012 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
26.2 | 1.0417 | 1.5 | 86 | 28.08 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
68.8 | 1.0417 | 1.5 | 87 | 29.148 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
10 | 0.69444 | 1 | 88 | 29.716 | 336571.5917 | 0.047391 | 7101960.1929 | 5 | 10000000 | 3456000 | 3750000 | 10851960.1929 | 0.77514
37.7 | 1.0417 | 1.5 | 89 | 30.784 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
11.6 | 0.80556 | 1.16 | 90 | 31.512 | 390423.0464 | 0.051434 | 7590791.3348 | 5.8 | 11600000 | 3456000 | 3750000 | 11340791.3348 | 0.81006
0 | 0 | 0 | 91 | 31.08 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
33.7 | 1.0417 | 1.5 | 92 | 32.148 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
9 | 0.625 | 0.9 | 93 | 32.616 | 302914.4326 | 0.044717 | 6774046.2561 | 4.5 | 9000000 | 3456000 | 3750000 | 10524046.2561 | 0.75172
8.4 | 0.58333 | 0.84 | 94 | 33.024 | 282720.1371 | 0.043048 | 6567516.6613 | 4.2 | 8400000 | 3456000 | 3750000 | 10317516.6613 | 0.73697
0.6 | 0.041667 | 0.06 | 95 | 32.652 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
0 | 0 | 0 | 96 | 32.22 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 97 | 31.788 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 98 | 31.356 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
3.2 | 0.22222 | 0.32 | 99 | 31.244 | 107702.9094 | 0.0253 | 4257053.1739 | 1.6 | 3200000 | 3456000 | 3750000 | 8007053.1739 | 0.57193
40.2 | 1.0417 | 1.5 | 100 | 32.312 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
9.2 | 0.63889 | 0.92 | 101 | 32.8 | 309645.8644 | 0.045262 | 6841185.9025 | 4.6 | 9200000 | 3456000 | 3750000 | 10591185.9025 | 0.75651
24.4 | 1.0417 | 1.5 | 102 | 33.868 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
16.2 | 1.0417 | 1.5 | 103 | 34.936 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
1.5 | 0.10417 | 0.15 | 104 | 34.654 | 50485.7388 | 0.016674 | 3027861.2026 | 0.75 | 1500000 | 3456000 | 3750000 | 6777861.2026 | 0.48413
37.2 | 1.0417 | 1.5 | 105 | 35.722 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
3 | 0.20833 | 0.3 | 106 | 35.59 | 100971.4775 | 0.024417 | 4135312.2152 | 1.5 | 3000000 | 3456000 | 3750000 | 7885312.2152 | 0.56324
0 | 0 | 0 | 107 | 35.158 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 108 | 34.726 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 109 | 34.294 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
1.1 | 0.076389 | 0.11 | 110 | 33.972 | 37022.8751 | 0.014058 | 2633576.3392 | 0.55 | 1100000 | 3456000 | 3750000 | 6383576.3392 | 0.45597
0.4 | 0.027778 | 0.04 | 111 | 33.58 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
8.2 | 0.56944 | 0.82 | 112 | 33.968 | 275988.7052 | 0.04248 | 6496865.8074 | 4.1 | 8200000 | 3456000 | 3750000 | 10246865.8074 | 0.73192
8.4 | 0.58333 | 0.84 | 113 | 34.376 | 282720.1371 | 0.043048 | 6567516.6613 | 4.2 | 8400000 | 3456000 | 3750000 | 10317516.6613 | 0.73697
1.8 | 0.125 | 0.18 | 114 | 34.124 | 60582.8865 | 0.018433 | 3286618.4834 | 0.9 | 1800000 | 3456000 | 3750000 | 7036618.4834 | 0.50262
0 | 0 | 0 | 115 | 33.692 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
4.2 | 0.29167 | 0.42 | 116 | 33.68 | 141360.0685 | 0.029386 | 4810530.6705 | 2.1 | 4200000 | 3456000 | 3750000 | 8560530.6705 | 0.61147
22.4 | 1.0417 | 1.5 | 117 | 34.748 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
15.4 | 1.0417 | 1.5 | 118 | 35.816 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
27.6 | 1.0417 | 1.5 | 119 | 36 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
4.8 | 0.33333 | 0.48 | 120 | 36 | 161554.364 | 0.031628 | 5108023.6078 | 2.4 | 4800000 | 3456000 | 3750000 | 8858023.6078 | 0.63272
0.8 | 0.055556 | 0.08 | 121 | 35.648 | 26925.7273 | 0.011799 | 2282064.5633 | 0.4 | 800000 | 3456000 | 3750000 | 6032064.5633 | 0.43086
0 | 0 | 0 | 122 | 35.216 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 123 | 34.784 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
19.8 | 1.0417 | 1.5 | 124 | 35.852 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.4 | 0.027778 | 0.04 | 125 | 35.46 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
0 | 0 | 0 | 126 | 35.028 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 127 | 34.596 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 128 | 34.164 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 129 | 33.732 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.4 | 0.027778 | 0.04 | 130 | 33.34 | 13462.8637 | 0.0080584 | 1670662.5388 | 0.2 | 400000 | 3456000 | 3750000 | 5420662.5388 | 0.38719
0 | 0 | 0 | 131 | 32.908 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 132 | 32.476 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 133 | 32.044 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 134 | 31.612 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 135 | 31.18 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.2 | 0.013889 | 0.02 | 136 | 30.768 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
0 | 0 | 0 | 137 | 30.336 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 138 | 29.904 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 139 | 29.472 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 140 | 29.04 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 141 | 28.608 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.2 | 0.013889 | 0.02 | 142 | 28.196 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
0.2 | 0.013889 | 0.02 | 143 | 27.784 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
0 | 0 | 0 | 144 | 27.352 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 145 | 26.92 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 146 | 26.488 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 147 | 26.056 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 148 | 25.624 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 149 | 25.192 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 150 | 24.76 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 151 | 24.328 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
7.4 | 0.51389 | 0.74 | 152 | 24.636 | 249062.9779 | 0.040144 | 6204268.2883 | 3.7 | 7400000 | 3456000 | 3750000 | 9954268.2883 | 0.71102
2.8 | 0.19444 | 0.28 | 153 | 24.484 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421
0 | 0 | 0 | 154 | 24.052 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 155 | 23.62 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 156 | 23.188 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 157 | 22.756 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 158 | 22.324 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 159 | 21.892 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 160 | 21.46 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 161 | 21.028 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 162 | 20.596 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 163 | 20.164 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 164 | 19.732 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 165 | 19.3 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 166 | 18.868 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 167 | 18.436 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 168 | 18.004 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
7 | 0.48611 | 0.7 | 169 | 18.272 | 235600.1142 | 0.038933 | 6051384.2332 | 3.5 | 7000000 | 3456000 | 3750000 | 9801384.2332 | 0.7001
0 | 0 | 0 | 170 | 17.84 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 171 | 17.408 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 172 | 16.976 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 173 | 16.544 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
1.4 | 0.097222 | 0.14 | 174 | 16.252 | 47120.0228 | 0.016053 | 2935341.1941 | 0.7 | 1400000 | 3456000 | 3750000 | 6685341.1941 | 0.47752
13.4 | 0.93056 | 1.34 | 175 | 17.16 | 451005.9329 | 0.055695 | 8097830.4211 | 6.7 | 13400000 | 3456000 | 3750000 | 11847830.4211 | 0.84627
4 | 0.27778 | 0.4 | 176 | 17.128 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
0 | 0 | 0 | 177 | 16.696 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 178 | 16.264 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 179 | 15.832 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 180 | 15.4 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 181 | 14.968 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 182 | 14.536 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 183 | 14.104 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 184 | 13.672 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 185 | 13.24 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 186 | 12.808 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 187 | 12.376 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.2 | 0.013889 | 0.02 | 188 | 11.964 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
0 | 0 | 0 | 189 | 11.532 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
1 | 0.069444 | 0.1 | 190 | 11.2 | 33657.1592 | 0.01334 | 2523046.647 | 0.5 | 1000000 | 3456000 | 3750000 | 6273046.647 | 0.44807
1.2 | 0.083333 | 0.12 | 191 | 10.888 | 40388.591 | 0.014747 | 2738701.4233 | 0.6 | 1200000 | 3456000 | 3750000 | 6488701.4233 | 0.46348
2.4 | 0.16667 | 0.24 | 192 | 10.696 | 80777.182 | 0.021595 | 3740548.2606 | 1.2 | 2400000 | 3456000 | 3750000 | 7490548.2606 | 0.53504
4 | 0.27778 | 0.4 | 193 | 10.664 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
0 | 0 | 0 | 194 | 10.232 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 195 | 9.8 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 196 | 9.368 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 197 | 8.936 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 198 | 8.504 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 199 | 8.072 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 200 | 7.64 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0.6 | 0.041667 | 0.06 | 201 | 7.268 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
0 | 0 | 0 | 202 | 6.836 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 203 | 6.404 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
8.4 | 0.58333 | 0.84 | 204 | 6.812 | 282720.1371 | 0.043048 | 6567516.6613 | 4.2 | 8400000 | 3456000 | 3750000 | 10317516.6613 | 0.73697
4 | 0.27778 | 0.4 | 205 | 6.78 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
4.2 | 0.29167 | 0.42 | 206 | 6.768 | 141360.0685 | 0.029386 | 4810530.6705 | 2.1 | 4200000 | 3456000 | 3750000 | 8560530.6705 | 0.61147
0 | 0 | 0 | 207 | 6.336 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 208 | 5.904 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 209 | 5.472 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 210 | 5.04 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 211 | 4.608 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 212 | 4.176 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 213 | 3.744 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 214 | 3.312 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 215 | 2.88 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 216 | 2.448 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 217 | 2.016 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
3.2 | 0.22222 | 0.32 | 218 | 1.904 | 107702.9094 | 0.0253 | 4257053.1739 | 1.6 | 3200000 | 3456000 | 3750000 | 8007053.1739 | 0.57193
14.6 | 1.0139 | 1.46 | 219 | 2.932 | 491394.524 | 0.058395 | 8415062.4334 | 7.3 | 14600000 | 3456000 | 3750000 | 12165062.4334 | 0.86893
24.4 | 1.0417 | 1.5 | 220 | 4 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
1.8 | 0.125 | 0.18 | 221 | 3.748 | 60582.8865 | 0.018433 | 3286618.4834 | 0.9 | 1800000 | 3456000 | 3750000 | 7036618.4834 | 0.50262
0 | 0 | 0 | 222 | 3.316 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 223 | 2.884 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 224 | 2.452 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 225 | 2.02 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 226 | 1.588 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 227 | 1.156 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 228 | 0.724 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 229 | 0.292 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786 | 1
2.8 | 0.19444 | 0.28 | 239 | 0 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421 | 1
10.4 | 0.72222 | 1.04 | 240 | 0.608 | 350034.4554 | 0.048427 | 7228012.8816 | 5.2 | 10400000 | 3456000 | 3750000 | 10978012.8816 | 0.78414
33.4 | 1.0417 | 1.5 | 241 | 1.676 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
26 | 1.0417 | 1.5 | 242 | 2.744 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
6 | 0.41667 | 0.6 | 243 | 2.912 | 201942.955 | 0.035763 | 5646631.6913 | 3 | 6000000 | 3456000 | 3750000 | 9396631.6913 | 0.67119
15.8 | 1.0417 | 1.5 | 244 | 3.98 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.8 | 0.055556 | 0.08 | 245 | 3.628 | 26925.7273 | 0.011799 | 2282064.5633 | 0.4 | 800000 | 3456000 | 3750000 | 6032064.5633 | 0.43086
2.4 | 0.16667 | 0.24 | 246 | 3.436 | 80777.182 | 0.021595 | 3740548.2606 | 1.2 | 2400000 | 3456000 | 3750000 | 7490548.2606 | 0.53504
0 | 0 | 0 | 247 | 3.004 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
1.6 | 0.11111 | 0.16 | 248 | 2.732 | 53851.4547 | 0.017276 | 3117043.133 | 0.8 | 1600000 | 3456000 | 3750000 | 6867043.133 | 0.4905
0 | 0 | 0 | 249 | 2.3 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
29.6 | 1.0417 | 1.5 | 250 | 3.368 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
13 | 0.90278 | 1.3 | 251 | 4.236 | 437543.0693 | 0.054771 | 7988593.9538 | 6.5 | 13000000 | 3456000 | 3750000 | 11738593.9538 | 0.83847
1.4 | 0.097222 | 0.14 | 252 | 3.944 | 47120.0228 | 0.016053 | 2935341.1941 | 0.7 | 1400000 | 3456000 | 3750000 | 6685341.1941 | 0.47752
0 | 0 | 0 | 253 | 3.512 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 254 | 3.08 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 255 | 2.648 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 256 | 2.216 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 257 | 1.784 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
2 | 0.13889 | 0.2 | 258 | 1.552 | 67314.3183 | 0.019533 | 3446101.0659 | 1 | 2000000 | 3456000 | 3750000 | 7196101.0659 | 0.51401
4 | 0.27778 | 0.4 | 259 | 1.52 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
2.8 | 0.19444 | 0.28 | 260 | 1.368 | 94240.0457 | 0.023507 | 4009008.791 | 1.4 | 2800000 | 3456000 | 3750000 | 7759008.791 | 0.55421
46.4 | 1.0417 | 1.5 | 261 | 2.436 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
86.8 | 1.0417 | 1.5 | 262 | 3.504 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
1.4 | 0.097222 | 0.14 | 263 | 3.212 | 47120.0228 | 0.016053 | 2935341.1941 | 0.7 | 1400000 | 3456000 | 3750000 | 6685341.1941 | 0.47752
4.2 | 0.29167 | 0.42 | 264 | 3.2 | 141360.0685 | 0.029386 | 4810530.6705 | 2.1 | 4200000 | 3456000 | 3750000 | 8560530.6705 | 0.61147
39.8 | 1.0417 | 1.5 | 265 | 4.268 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
29.8 | 1.0417 | 1.5 | 266 | 5.336 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
11.8 | 0.81944 | 1.18 | 267 | 6.084 | 397154.4783 | 0.051921 | 7649194.4552 | 5.9 | 11800000 | 3456000 | 3750000 | 11399194.4552 | 0.81423
1.6 | 0.11111 | 0.16 | 268 | 5.812 | 53851.4547 | 0.017276 | 3117043.133 | 0.8 | 1600000 | 3456000 | 3750000 | 6867043.133 | 0.4905
0 | 0 | 0 | 269 | 5.38 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 270 | 4.948 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 271 | 4.516 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 272 | 4.084 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 273 | 3.652 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 274 | 3.22 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 275 | 2.788 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 276 | 2.356 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 277 | 1.924 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 278 | 1.492 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
4 | 0.27778 | 0.4 | 279 | 1.46 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
15.6 | 1.0417 | 1.5 | 280 | 2.528 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
9.2 | 0.63889 | 0.92 | 281 | 3.016 | 309645.8644 | 0.045262 | 6841185.9025 | 4.6 | 9200000 | 3456000 | 3750000 | 10591185.9025 | 0.75651
26.4 | 1.0417 | 1.5 | 282 | 4.084 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
27 | 1.0417 | 1.5 | 283 | 5.152 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
37.6 | 1.0417 | 1.5 | 284 | 6.22 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.8 | 0.055556 | 0.08 | 285 | 5.868 | 26925.7273 | 0.011799 | 2282064.5633 | 0.4 | 800000 | 3456000 | 3750000 | 6032064.5633 | 0.43086
0.6 | 0.041667 | 0.06 | 286 | 5.496 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
0 | 0 | 0 | 287 | 5.064 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 288 | 4.632 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
14.2 | 0.98611 | 1.42 | 289 | 5.62 | 477931.6603 | 0.057506 | 8310987.5712 | 7.1 | 14200000 | 3456000 | 3750000 | 12060987.5712 | 0.8615
6.4 | 0.44444 | 0.64 | 290 | 5.828 | 215405.8187 | 0.037058 | 5812702.185 | 3.2 | 6400000 | 3456000 | 3750000 | 9562702.185 | 0.68305
23.4 | 1.0417 | 1.5 | 291 | 6.896 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0.6 | 0.041667 | 0.06 | 292 | 6.524 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
10.2 | 0.70833 | 1.02 | 293 | 7.112 | 343303.0236 | 0.047912 | 7165329.2595 | 5.1 | 10200000 | 3456000 | 3750000 | 10915329.2595 | 0.77967
4 | 0.27778 | 0.4 | 294 | 7.08 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
9.8 | 0.68056 | 0.98 | 295 | 7.628 | 329840.1599 | 0.046866 | 7037884.3647 | 4.9 | 9800000 | 3456000 | 3750000 | 10787884.3647 | 0.77056
0 | 0 | 0 | 296 | 7.196 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
5.8 | 0.40278 | 0.58 | 297 | 7.344 | 195211.5232 | 0.035102 | 5561297.8149 | 2.9 | 5800000 | 3456000 | 3750000 | 9311297.8149 | 0.66509
4 | 0.27778 | 0.4 | 298 | 7.312 | 134628.6367 | 0.028607 | 4706195.4447 | 2 | 4000000 | 3456000 | 3750000 | 8456195.4447 | 0.60401
0 | 0 | 0 | 299 | 6.88 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
6.8 | 0.47222 | 0.68 | 300 | 7.128 | 228868.6824 | 0.038316 | 5973127.4264 | 3.4 | 6800000 | 3456000 | 3750000 | 9723127.4264 | 0.69451
39 | 1.0417 | 1.5 | 301 | 8.196 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
40.6 | 1.0417 | 1.5 | 302 | 9.264 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
35.4 | 1.0417 | 1.5 | 303 | 10.332 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
21.2 | 1.0417 | 1.5 | 304 | 11.4 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
1.2 | 0.083333 | 0.12 | 305 | 11.088 | 40388.591 | 0.014747 | 2738701.4233 | 0.6 | 1200000 | 3456000 | 3750000 | 6488701.4233 | 0.46348
0 | 0 | 0 | 306 | 10.656 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 307 | 10.224 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
3.4 | 0.23611 | 0.34 | 308 | 10.132 | 114434.3412 | 0.026158 | 4374666.4164 | 1.7 | 3400000 | 3456000 | 3750000 | 8124666.4164 | 0.58033
6 | 0.41667 | 0.6 | 309 | 10.3 | 201942.955 | 0.035763 | 5646631.6913 | 3 | 6000000 | 3456000 | 3750000 | 9396631.6913 | 0.67119
44.2 | 1.0417 | 1.5 | 310 | 11.368 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
2.2 | 0.15278 | 0.22 | 311 | 11.156 | 74045.7502 | 0.020585 | 3597017.6124 | 1.1 | 2200000 | 3456000 | 3750000 | 7347017.6124 | 0.52479
1.6 | 0.11111 | 0.16 | 312 | 10.884 | 53851.4547 | 0.017276 | 3117043.133 | 0.8 | 1600000 | 3456000 | 3750000 | 6867043.133 | 0.4905
0 | 0 | 0 | 313 | 10.452 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
20.5 | 1.0417 | 1.5 | 314 | 11.52 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
18.8 | 1.0417 | 1.5 | 315 | 12.588 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
59 | 1.0417 | 1.5 | 316 | 13.656 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
11.4 | 0.79167 | 1.14 | 317 | 14.364 | 383691.6146 | 0.050943 | 7531826.3883 | 5.7 | 11400000 | 3456000 | 3750000 | 11281826.3883 | 0.80584
0.6 | 0.041667 | 0.06 | 318 | 13.992 | 20194.2955 | 0.010072 | 2005015.1037 | 0.3 | 600000 | 3456000 | 3750000 | 5755015.1037 | 0.41107
6 | 0.41667 | 0.6 | 319 | 14.16 | 201942.955 | 0.035763 | 5646631.6913 | 3 | 6000000 | 3456000 | 3750000 | 9396631.6913 | 0.67119
55.4 | 1.0417 | 1.5 | 320 | 15.228 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
6.2 | 0.43056 | 0.62 | 321 | 15.416 | 208674.3869 | 0.036415 | 5730407.4353 | 3.1 | 6200000 | 3456000 | 3750000 | 9480407.4353 | 0.67717
0 | 0 | 0 | 322 | 14.984 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 323 | 14.552 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 324 | 14.12 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 325 | 13.688 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 326 | 13.256 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 327 | 12.824 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 328 | 12.392 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 329 | 11.96 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 330 | 11.528 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 331 | 11.096 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 332 | 10.664 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 333 | 10.232 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
13 | 0.90278 | 1.3 | 334 | 11.1 | 437543.0693 | 0.054771 | 7988593.9538 | 6.5 | 13000000 | 3456000 | 3750000 | 11738593.9538 | 0.83847
34.6 | 1.0417 | 1.5 | 335 | 12.168 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
27.4 | 1.0417 | 1.5 | 336 | 13.236 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
32.6 | 1.0417 | 1.5 | 337 | 14.304 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
27.2 | 1.0417 | 1.5 | 338 | 15.372 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
33.8 | 1.0417 | 1.5 | 339 | 16.44 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
22.4 | 1.0417 | 1.5 | 340 | 17.508 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
37.2 | 1.0417 | 1.5 | 341 | 18.576 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
27 | 1.0417 | 1.5 | 342 | 19.644 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
4.8 | 0.33333 | 0.48 | 343 | 19.692 | 161554.364 | 0.031628 | 5108023.6078 | 2.4 | 4800000 | 3456000 | 3750000 | 8858023.6078 | 0.63272
12.2 | 0.84722 | 1.22 | 344 | 20.48 | 410617.3419 | 0.052885 | 7764373.2095 | 6.1 | 12200000 | 3456000 | 3750000 | 11514373.2095 | 0.82246
3.4 | 0.23611 | 0.34 | 345 | 20.388 | 114434.3412 | 0.026158 | 4374666.4164 | 1.7 | 3400000 | 3456000 | 3750000 | 8124666.4164 | 0.58033
23.8 | 1.0417 | 1.5 | 346 | 21.456 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
0 | 0 | 0 | 347 | 21.024 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
2.4 | 0.16667 | 0.24 | 348 | 20.832 | 80777.182 | 0.021595 | 3740548.2606 | 1.2 | 2400000 | 3456000 | 3750000 | 7490548.2606 | 0.53504
3 | 0.20833 | 0.3 | 349 | 20.7 | 100971.4775 | 0.024417 | 4135312.2152 | 1.5 | 3000000 | 3456000 | 3750000 | 7885312.2152 | 0.56324
2.2 | 0.15278 | 0.22 | 350 | 20.488 | 74045.7502 | 0.020585 | 3597017.6124 | 1.1 | 2200000 | 3456000 | 3750000 | 7347017.6124 | 0.52479
21.8 | 1.0417 | 1.5 | 351 | 21.556 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
25.5 | 1.0417 | 1.5 | 352 | 22.624 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
31.8 | 1.0417 | 1.5 | 353 | 23.692 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
22.6 | 1.0417 | 1.5 | 354 | 24.76 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
9 | 0.625 | 0.9 | 355 | 25.228 | 302914.4326 | 0.044717 | 6774046.2561 | 4.5 | 9000000 | 3456000 | 3750000 | 10524046.2561 | 0.75172
35.8 | 1.0417 | 1.5 | 356 | 26.296 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
9.4 | 0.65278 | 0.94 | 357 | 26.804 | 316377.2962 | 0.045802 | 6907521.4948 | 4.7 | 9400000 | 3456000 | 3750000 | 10657521.4948 | 0.76125
0 | 0 | 0 | 358 | 26.372 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 359 | 25.94 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
26.2 | 1.0417 | 1.5 | 360 | 27.008 | 504857.3876 | 0.059273 | 8517561.9968 | 7.5 | 15000000 | 3456000 | 3750000 | 12267561.9968 | 0.87625
1.6 | 0.11111 | 0.16 | 361 | 26.736 | 53851.4547 | 0.017276 | 3117043.133 | 0.8 | 1600000 | 3456000 | 3750000 | 6867043.133 | 0.4905
0.2 | 0.013889 | 0.02 | 362 | 26.324 | 6731.4318 | 0.0055039 | 1223030.7852 | 0.1 | 200000 | 3456000 | 3750000 | 4973030.7852 | 0.35522
0 | 0 | 0 | 363 | 25.892 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 364 | 25.46 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786
0 | 0 | 0 | 365 | 25.028 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3750000 | 3750000 | 0.26786

## Cost
Reference Cost | 105000 | $
[9 empty] | Total Cost | 46662.3777
[9 empty] | Cost Percentage | 44.4404
|  | Purchasing Costs | [6 empty] | Maintenance Costs (Per Year) | [5 empty] | Base Shipping Cost | 85 | $/day
|  | Catchment | Whole roof | N/A | 350 | $ | plumbing cost? |  | Item |  | # of Maintainence | Cost Per Maintainence | Total Cost |  | Days Without Water | 19 | days
|  | Catchment Tank | 1500 | L | 500 | $ |  |  | Filter 1 |  | 7 | 75 | 525 | $ | Emergency Water Cost | 1615 | $
|  | Storage Tank | 36 | m^3 | 9900 | $ |  |  | Filter 5 |  | 7 | 60 | 420 | $
|  | Storage Tower | 0 | m | 0 | $ |  |  | Filter 200 |  | 7 | 50 | 350 | $
|  | Piping there | 63.9316 | m | 2876.9222 | $ |  | Chlorine | Ozone or Chlorine |  | 7 | 100 | 700 | $
|  | Piping back | 63.4429 | m | 2854.9299 | $ |  |  | UV |  | 1 | 80 | 80 | $
|  | AC piping | N/A | m | 0 | $ |  |  | Pump |  | 0.068094 | 3250 | 221.3051 | $
|  | Filter 1 | y | N/A | 125 | $ |  | Solar | Solar Or Diesel |  | 4 | 0 | 0 | $
|  | Filter 5 | y | N/A | 110 | $ |  |  | Generator |  | 0 | 0 | 0 | $
|  | Filter 200 | y | N/A | 100 | $ |  |  | Emergency Water |  | 19 | 85 | 1615 | $
|  | Ozone or Chlorine | Chlorine | N/A | 700 | $ | [7 empty] | $
|  | UV | 40 | W | 600 | $ | [7 empty] | $
|  | Pump | Pump C | N/A | 3250 | $ | [7 empty] | $
|  | Solar or Diesel | Solar | N/A | 0 | N/A | [7 empty] | $
|  | Solar Panels | HES-260 | N/A | 2200 | $ | [7 empty] | $
|  | Batteries | 3 | # | 1170 | $ |  |  | Total |  |  |  | 3911.3051 | $
|  | Inverter | yes | N/A | 2369 | $ |  |  |  |  | Total 5 Year |  | 19556.5256 | $
|  | Generator | no | N/A | 0 | $
|  | Total |  |  | 27105.8521 | $ |  |  |  |  | Notes: Solar does not have cost per maintainence on Doc
Ozone does not have Cost Per Maintainence on Doc
momoomom
momomomom
momomomom
momomomom
momomomom
momomomom
momomommo
momomoomo
momomo
mom
mommo
mo
m
m
m
m
m
m
o
o
m

## Satisfaction Values
Attribute | Paramater | Equation | Value | Weight | Min | Max | Units | Satisfaction | percent? | Weighted sum
Consumption | C |  | 432 | 0.13 | 150 | 640 | L/Day | 0.6175 | 61.7502 | 8.0275
Maintenance occurances | M |  | 20 | 0.15 | 10 | 45 | #/year | 0.81174 | 81.1745 | 12.1762
On demand flow rate | Q0 |  | 28.5869 | 0.13 | 15 | 40 | L/min | 0.56808 | 56.8079 | 7.385
Relative cost | Cr |  | 44.4404 | 0.22 | 20 | 110 | %relative to shipping water | 0.82881 | 82.8814 | 18.2339
Health & environmental risk | E |  | 14.161 | 0.07 | 1 | 32 | N/A | 0.61741 | 61.741 | 4.3219
Power system greenhouse gas emissions | G |  | 69.1926 | 0.05 | 10 | 105 | %relative to shipping water | 0.31145 | 31.1448 | 1.5572
Reliability | R |  | 346 | 0.1 | 210 | 365 | days/year | 0.96338 | 96.3381 | 9.6338
Land use | U |  | 0.10862 | 0.15 | 0 | 1 | %impact relative to worst case | 0.83021 | 83.0208 | 12.4531
1
Total satisfaction | 73.7887

## More accurate Energy (Solar)
|  | Parameters | [6 empty] | Pump Chosen | Pump C | Pump |  |  | Battery |  |  |  | Density | 1000 | [kg/m^3]
|  | Daily Consumption |  | 432 | L/Day | [5 empty] | Pressure | 336.5716 | kPa | # of Batteries |  | 3 |  | Gravity | 9.81 | [m/s^2]
|  | Catchment Area |  | 100 | m^2 | [5 empty] | Qmax | 136.5 | LPM | Capacity |  | 2000 | Wh
|  | Collection Volume |  | 1.5 | m^3 | [5 empty] | Efficiency | 70 | % | Effiecency in |  | 0.96 | % | Heating Value Diesel | 40 | [MJ/L]
|  | Storage Volume |  | 36 | m^3 | [12 empty] | Efficiency of Generator | 35% | [ ]
|  | Distance |  | 63.9316 | m | [5 empty] | Contact Time | 10 | [min] | UV Lamp Size | 40 | [W]
|  | Elavation Of Base |  | 21.5 | m | [5 empty] | CT_Ozone | 50 | [mg min/L] |  |  |  |  | Pump Cont.
|  | Usage Day |  | 31 | [6 empty] | Energy for O3 | 2 | [MJ / g] | Pump Q | 22.6403 | LPM |  | A | 0.72
[15 empty] | 1358.4186 | LPH |  | B | 0.55
Total Litres
Daily Rainfall | Qin | Qin | Day | Vstorage | M energy | Effiency | E_energy | Energy Needed Inverter | g_Ozone | E_Energy Ozone | E_Batt UV | E_No_Ozone | E_total needed from batteries | 166500
[mm] | [LPM] | [m^3 / day] |  | [m^3] | [J] | [%] | [J] | [J] | [g] | [J] | [J] | [J] | [J]
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total Time | 122.569 | Hours
7.8 | 0.54167 | 0.78 | 1 | 0.78 | 164513.7 | 0.041325 | 6352644.4742 | 6905048.3416 | 3.9 | 7800000 | 3456000 | 10361048.3416 | 10361048.3416
1 | 0.069444 | 0.1 | 2 | 0.88 | 21091.5 | 0.01334 | 2523046.647 | 2742442.0076 | 0.5 | 1000000 | 3456000 | 6198442.0076 | 6198442.0076 | 14.6856
13.4 | 0.93056 | 1.34 | 3 | 2.22 | 282626.1 | 0.055695 | 8097830.4211 | 8801989.5882 | 6.7 | 13400000 | 3456000 | 12257989.5882 | 12257989.5882
64.2 | 1.0417 | 1.5 | 4 | 3.72 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
32.2 | 1.0417 | 1.5 | 5 | 5.22 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
2.8 | 0.19444 | 0.28 | 6 | 5.5 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
0 | 0 | 0 | 7 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 8 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.8 | 0.055556 | 0.08 | 9 | 5.58 | 16873.2 | 0.011799 | 2282064.5633 | 2480504.9601 | 0.4 | 800000 | 3456000 | 5936504.9601 | 5936504.9601
0 | 0 | 0 | 10 | 5.58 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 11 | 5.58 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 12 | 5.58 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 13 | 5.58 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.4 | 0.027778 | 0.04 | 14 | 5.62 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
35.4 | 1.0417 | 1.5 | 15 | 7.12 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
6 | 0.41667 | 0.6 | 16 | 7.72 | 126549 | 0.035763 | 5646631.6913 | 6137643.1427 | 3 | 6000000 | 3456000 | 9593643.1427 | 9593643.1427
20.4 | 1.0417 | 1.5 | 17 | 9.22 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
16.6 | 1.0417 | 1.5 | 18 | 10.72 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
2.6 | 0.18056 | 0.26 | 19 | 10.98 | 54837.9 | 0.022568 | 3877627.2231 | 4214812.1991 | 1.3 | 2600000 | 3456000 | 7670812.1991 | 7670812.1991
0.4 | 0.027778 | 0.04 | 20 | 11.02 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
18.4 | 1.0417 | 1.5 | 21 | 12.52 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
14 | 0.97222 | 1.4 | 22 | 13.92 | 295281 | 0.057058 | 8258338.0055 | 8976454.3538 | 7 | 14000000 | 3456000 | 12432454.3538 | 12432454.3538
90.8 | 1.0417 | 1.5 | 23 | 15.42 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
40 | 1.0417 | 1.5 | 24 | 16.92 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
1.8 | 0.125 | 0.18 | 25 | 17.1 | 37964.7 | 0.018433 | 3286618.4834 | 3572411.395 | 0.9 | 1800000 | 3456000 | 7028411.395 | 7028411.395
2.8 | 0.19444 | 0.28 | 26 | 17.38 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
2.8 | 0.19444 | 0.28 | 27 | 17.66 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
0 | 0 | 0 | 28 | 17.66 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 29 | 17.66 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.6 | 0.041667 | 0.06 | 30 | 17.72 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
5.8 | 0.40278 | 0.58 | 31 | 18.3 | 122330.7 | 0.035102 | 5561297.8149 | 6044888.9292 | 2.9 | 5800000 | 3456000 | 9500888.9292 | 9500888.9292
8 | 0.55556 | 0.8 | 32 | 18.668 | 168732 | 0.041906 | 6425254.2184 | 6983971.9766 | 4 | 8000000 | 3456000 | 10439971.9766 | 10439971.9766
27 | 1.0417 | 1.5 | 33 | 19.736 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.6 | 0.041667 | 0.06 | 34 | 19.364 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
36 | 1.0417 | 1.5 | 35 | 20.432 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
27.2 | 1.0417 | 1.5 | 36 | 21.5 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
28.2 | 1.0417 | 1.5 | 37 | 22.568 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
39.2 | 1.0417 | 1.5 | 38 | 23.636 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
6.6 | 0.45833 | 0.66 | 39 | 23.864 | 139203.9 | 0.037691 | 5893586.9827 | 6406072.8073 | 3.3 | 6600000 | 3456000 | 9862072.8073 | 9862072.8073
3.2 | 0.22222 | 0.32 | 40 | 23.752 | 67492.8 | 0.0253 | 4257053.1739 | 4627231.7108 | 1.6 | 3200000 | 3456000 | 8083231.7108 | 8083231.7108
0.2 | 0.013889 | 0.02 | 41 | 23.34 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
19.6 | 1.0417 | 1.5 | 42 | 24.408 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
30.4 | 1.0417 | 1.5 | 43 | 25.476 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
19 | 1.0417 | 1.5 | 44 | 26.544 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.2 | 0.013889 | 0.02 | 45 | 26.132 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
0 | 0 | 0 | 46 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 47 | 25.268 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 48 | 24.836 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
4 | 0.27778 | 0.4 | 49 | 24.804 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
11 | 0.76389 | 1.1 | 50 | 25.472 | 232006.5 | 0.049949 | 7412149.0722 | 8056683.7741 | 5.5 | 11000000 | 3456000 | 11512683.7741 | 11512683.7741
0.4 | 0.027778 | 0.04 | 51 | 25.08 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
0 | 0 | 0 | 52 | 24.648 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 53 | 24.216 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 54 | 23.784 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.2 | 0.013889 | 0.02 | 55 | 23.372 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
4.6 | 0.31944 | 0.46 | 56 | 23.4 | 97020.9 | 0.030895 | 5011266.7336 | 5447029.0583 | 2.3 | 4600000 | 3456000 | 8903029.0583 | 8903029.0583
8.8 | 0.61111 | 0.88 | 57 | 23.848 | 185605.2 | 0.044166 | 6706074.7466 | 7289211.681 | 4.4 | 8800000 | 3456000 | 10745211.681 | 10745211.681
0.4 | 0.027778 | 0.04 | 58 | 23.456 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
0 | 0 | 0 | 59 | 23.024 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
1.2 | 0.083333 | 0.12 | 60 | 22.712 | 25309.8 | 0.014747 | 2738701.4233 | 2976849.3732 | 0.6 | 1200000 | 3456000 | 6432849.3732 | 6432849.3732
0 | 0 | 0 | 61 | 22.28 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 62 | 21.848 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.4 | 0.027778 | 0.04 | 63 | 21.456 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
1.8 | 0.125 | 0.18 | 64 | 21.204 | 37964.7 | 0.018433 | 3286618.4834 | 3572411.395 | 0.9 | 1800000 | 3456000 | 7028411.395 | 7028411.395
0.8 | 0.055556 | 0.08 | 65 | 20.852 | 16873.2 | 0.011799 | 2282064.5633 | 2480504.9601 | 0.4 | 800000 | 3456000 | 5936504.9601 | 5936504.9601
0 | 0 | 0 | 66 | 20.42 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.4 | 0.027778 | 0.04 | 67 | 20.028 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
0.4 | 0.027778 | 0.04 | 68 | 19.636 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
2.8 | 0.19444 | 0.28 | 69 | 19.484 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
13.6 | 0.94444 | 1.36 | 70 | 20.412 | 286844.4 | 0.056152 | 8151769.053 | 8860618.5358 | 6.8 | 13600000 | 3456000 | 12316618.5358 | 12316618.5358
8.6 | 0.59722 | 0.86 | 71 | 20.84 | 181386.9 | 0.04361 | 6637241.9437 | 7214393.4171 | 4.3 | 8600000 | 3456000 | 10670393.4171 | 10670393.4171
17.4 | 1.0417 | 1.5 | 72 | 21.908 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.6 | 0.041667 | 0.06 | 73 | 21.536 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
0 | 0 | 0 | 74 | 21.104 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 75 | 20.672 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 76 | 20.24 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
31 | 1.0417 | 1.5 | 77 | 21.308 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
35.4 | 1.0417 | 1.5 | 78 | 22.376 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
28.6 | 1.0417 | 1.5 | 79 | 23.444 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0 | 0 | 0 | 80 | 23.012 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
7 | 0.48611 | 0.7 | 81 | 23.28 | 147640.5 | 0.038933 | 6051384.2332 | 6577591.5579 | 3.5 | 7000000 | 3456000 | 10033591.5579 | 10033591.5579
9.6 | 0.66667 | 0.96 | 82 | 23.808 | 202478.4 | 0.046337 | 6973079.3422 | 7579434.0676 | 4.8 | 9600000 | 3456000 | 11035434.0676 | 11035434.0676
18.2 | 1.0417 | 1.5 | 83 | 24.876 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
104.4 | 1.0417 | 1.5 | 84 | 25.944 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
33.2 | 1.0417 | 1.5 | 85 | 27.012 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
26.2 | 1.0417 | 1.5 | 86 | 28.08 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
68.8 | 1.0417 | 1.5 | 87 | 29.148 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
10 | 0.69444 | 1 | 88 | 29.716 | 210915 | 0.047391 | 7101960.1929 | 7719521.9488 | 5 | 10000000 | 3456000 | 11175521.9488 | 11175521.9488
37.7 | 1.0417 | 1.5 | 89 | 30.784 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
11.6 | 0.80556 | 1.16 | 90 | 31.512 | 244661.4 | 0.051434 | 7590791.3348 | 8250860.1465 | 5.8 | 11600000 | 3456000 | 11706860.1465 | 11706860.1465
0 | 0 | 0 | 91 | 31.08 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
33.7 | 1.0417 | 1.5 | 92 | 32.148 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
9 | 0.625 | 0.9 | 93 | 32.616 | 189823.5 | 0.044717 | 6774046.2561 | 7363093.7566 | 4.5 | 9000000 | 3456000 | 10819093.7566 | 10819093.7566
8.4 | 0.58333 | 0.84 | 94 | 33.024 | 177168.6 | 0.043048 | 6567516.6613 | 7138605.0666 | 4.2 | 8400000 | 3456000 | 10594605.0666 | 10594605.0666
0.6 | 0.041667 | 0.06 | 95 | 32.652 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
0 | 0 | 0 | 96 | 32.22 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 97 | 31.788 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 98 | 31.356 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
3.2 | 0.22222 | 0.32 | 99 | 31.244 | 67492.8 | 0.0253 | 4257053.1739 | 4627231.7108 | 1.6 | 3200000 | 3456000 | 8083231.7108 | 8083231.7108
40.2 | 1.0417 | 1.5 | 100 | 32.312 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
9.2 | 0.63889 | 0.92 | 101 | 32.8 | 194041.8 | 0.045262 | 6841185.9025 | 7436071.6332 | 4.6 | 9200000 | 3456000 | 10892071.6332 | 10892071.6332
24.4 | 1.0417 | 1.5 | 102 | 33.868 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
16.2 | 1.0417 | 1.5 | 103 | 34.936 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
1.5 | 0.10417 | 0.15 | 104 | 34.654 | 31637.25 | 0.016674 | 3027861.2026 | 3291153.4811 | 0.75 | 1500000 | 3456000 | 6747153.4811 | 6747153.4811
37.2 | 1.0417 | 1.5 | 105 | 35.722 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
3 | 0.20833 | 0.3 | 106 | 35.59 | 63274.5 | 0.024417 | 4135312.2152 | 4494904.5817 | 1.5 | 3000000 | 3456000 | 7950904.5817 | 7950904.5817
0 | 0 | 0 | 107 | 35.158 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 108 | 34.726 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 109 | 34.294 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
1.1 | 0.076389 | 0.11 | 110 | 33.972 | 23200.65 | 0.014058 | 2633576.3392 | 2862582.9774 | 0.55 | 1100000 | 3456000 | 6318582.9774 | 6318582.9774
0.4 | 0.027778 | 0.04 | 111 | 33.58 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
8.2 | 0.56944 | 0.82 | 112 | 33.968 | 172950.3 | 0.04248 | 6496865.8074 | 7061810.6602 | 4.1 | 8200000 | 3456000 | 10517810.6602 | 10517810.6602
8.4 | 0.58333 | 0.84 | 113 | 34.376 | 177168.6 | 0.043048 | 6567516.6613 | 7138605.0666 | 4.2 | 8400000 | 3456000 | 10594605.0666 | 10594605.0666
1.8 | 0.125 | 0.18 | 114 | 34.124 | 37964.7 | 0.018433 | 3286618.4834 | 3572411.395 | 0.9 | 1800000 | 3456000 | 7028411.395 | 7028411.395
0 | 0 | 0 | 115 | 33.692 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
4.2 | 0.29167 | 0.42 | 116 | 33.68 | 88584.3 | 0.029386 | 4810530.6705 | 5228837.6853 | 2.1 | 4200000 | 3456000 | 8684837.6853 | 8684837.6853
22.4 | 1.0417 | 1.5 | 117 | 34.748 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
15.4 | 1.0417 | 1.5 | 118 | 35.816 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
27.6 | 1.0417 | 1.5 | 119 | 36 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
4.8 | 0.33333 | 0.48 | 120 | 36 | 101239.2 | 0.031628 | 5108023.6078 | 5552199.5737 | 2.4 | 4800000 | 3456000 | 9008199.5737 | 9008199.5737
0.8 | 0.055556 | 0.08 | 121 | 35.648 | 16873.2 | 0.011799 | 2282064.5633 | 2480504.9601 | 0.4 | 800000 | 3456000 | 5936504.9601 | 5936504.9601
0 | 0 | 0 | 122 | 35.216 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 123 | 34.784 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
19.8 | 1.0417 | 1.5 | 124 | 35.852 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.4 | 0.027778 | 0.04 | 125 | 35.46 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
0 | 0 | 0 | 126 | 35.028 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 127 | 34.596 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 128 | 34.164 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 129 | 33.732 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.4 | 0.027778 | 0.04 | 130 | 33.34 | 8436.6 | 0.0080584 | 1670662.5388 | 1815937.5421 | 0.2 | 400000 | 3456000 | 5271937.5421 | 5271937.5421
0 | 0 | 0 | 131 | 32.908 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 132 | 32.476 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 133 | 32.044 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 134 | 31.612 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 135 | 31.18 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.2 | 0.013889 | 0.02 | 136 | 30.768 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
0 | 0 | 0 | 137 | 30.336 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 138 | 29.904 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 139 | 29.472 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 140 | 29.04 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 141 | 28.608 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.2 | 0.013889 | 0.02 | 142 | 28.196 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
0.2 | 0.013889 | 0.02 | 143 | 27.784 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
0 | 0 | 0 | 144 | 27.352 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 145 | 26.92 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 146 | 26.488 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 147 | 26.056 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 148 | 25.624 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 149 | 25.192 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 150 | 24.76 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 151 | 24.328 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
7.4 | 0.51389 | 0.74 | 152 | 24.636 | 156077.1 | 0.040144 | 6204268.2883 | 6743769.8786 | 3.7 | 7400000 | 3456000 | 10199769.8786 | 10199769.8786
2.8 | 0.19444 | 0.28 | 153 | 24.484 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
0 | 0 | 0 | 154 | 24.052 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 155 | 23.62 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 156 | 23.188 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 157 | 22.756 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 158 | 22.324 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 159 | 21.892 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 160 | 21.46 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 161 | 21.028 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 162 | 20.596 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 163 | 20.164 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 164 | 19.732 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 165 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 166 | 18.868 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 167 | 18.436 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 168 | 18.004 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
7 | 0.48611 | 0.7 | 169 | 18.272 | 147640.5 | 0.038933 | 6051384.2332 | 6577591.5579 | 3.5 | 7000000 | 3456000 | 10033591.5579 | 10033591.5579
0 | 0 | 0 | 170 | 17.84 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 171 | 17.408 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 172 | 16.976 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 173 | 16.544 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
1.4 | 0.097222 | 0.14 | 174 | 16.252 | 29528.1 | 0.016053 | 2935341.1941 | 3190588.2545 | 0.7 | 1400000 | 3456000 | 6646588.2545 | 6646588.2545
13.4 | 0.93056 | 1.34 | 175 | 17.16 | 282626.1 | 0.055695 | 8097830.4211 | 8801989.5882 | 6.7 | 13400000 | 3456000 | 12257989.5882 | 12257989.5882
4 | 0.27778 | 0.4 | 176 | 17.128 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
0 | 0 | 0 | 177 | 16.696 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 178 | 16.264 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 179 | 15.832 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 180 | 15.4 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 181 | 14.968 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 182 | 14.536 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 183 | 14.104 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 184 | 13.672 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 185 | 13.24 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 186 | 12.808 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 187 | 12.376 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.2 | 0.013889 | 0.02 | 188 | 11.964 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
0 | 0 | 0 | 189 | 11.532 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
1 | 0.069444 | 0.1 | 190 | 11.2 | 21091.5 | 0.01334 | 2523046.647 | 2742442.0076 | 0.5 | 1000000 | 3456000 | 6198442.0076 | 6198442.0076
1.2 | 0.083333 | 0.12 | 191 | 10.888 | 25309.8 | 0.014747 | 2738701.4233 | 2976849.3732 | 0.6 | 1200000 | 3456000 | 6432849.3732 | 6432849.3732
2.4 | 0.16667 | 0.24 | 192 | 10.696 | 50619.6 | 0.021595 | 3740548.2606 | 4065813.3267 | 1.2 | 2400000 | 3456000 | 7521813.3267 | 7521813.3267
4 | 0.27778 | 0.4 | 193 | 10.664 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
0 | 0 | 0 | 194 | 10.232 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 195 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 196 | 9.368 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 197 | 8.936 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 198 | 8.504 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 199 | 8.072 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 200 | 7.64 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0.6 | 0.041667 | 0.06 | 201 | 7.268 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
0 | 0 | 0 | 202 | 6.836 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 203 | 6.404 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
8.4 | 0.58333 | 0.84 | 204 | 6.812 | 177168.6 | 0.043048 | 6567516.6613 | 7138605.0666 | 4.2 | 8400000 | 3456000 | 10594605.0666 | 10594605.0666
4 | 0.27778 | 0.4 | 205 | 6.78 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
4.2 | 0.29167 | 0.42 | 206 | 6.768 | 88584.3 | 0.029386 | 4810530.6705 | 5228837.6853 | 2.1 | 4200000 | 3456000 | 8684837.6853 | 8684837.6853
0 | 0 | 0 | 207 | 6.336 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 208 | 5.904 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 209 | 5.472 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 210 | 5.04 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 211 | 4.608 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 212 | 4.176 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 213 | 3.744 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 214 | 3.312 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 215 | 2.88 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 216 | 2.448 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 217 | 2.016 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
3.2 | 0.22222 | 0.32 | 218 | 1.904 | 67492.8 | 0.0253 | 4257053.1739 | 4627231.7108 | 1.6 | 3200000 | 3456000 | 8083231.7108 | 8083231.7108
14.6 | 1.0139 | 1.46 | 219 | 2.932 | 307935.9 | 0.058395 | 8415062.4334 | 9146806.9928 | 7.3 | 14600000 | 3456000 | 12602806.9928 | 12602806.9928
24.4 | 1.0417 | 1.5 | 220 | 4 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
1.8 | 0.125 | 0.18 | 221 | 3.748 | 37964.7 | 0.018433 | 3286618.4834 | 3572411.395 | 0.9 | 1800000 | 3456000 | 7028411.395 | 7028411.395
0 | 0 | 0 | 222 | 3.316 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 223 | 2.884 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 224 | 2.452 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 225 | 2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 226 | 1.588 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 227 | 1.156 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 228 | 0.724 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 229 | 0.292 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
2.8 | 0.19444 | 0.28 | 239 | 0 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
10.4 | 0.72222 | 1.04 | 240 | 0.608 | 219351.6 | 0.048427 | 7228012.8816 | 7856535.7409 | 5.2 | 10400000 | 3456000 | 11312535.7409 | 11312535.7409
33.4 | 1.0417 | 1.5 | 241 | 1.676 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
26 | 1.0417 | 1.5 | 242 | 2.744 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
6 | 0.41667 | 0.6 | 243 | 2.912 | 126549 | 0.035763 | 5646631.6913 | 6137643.1427 | 3 | 6000000 | 3456000 | 9593643.1427 | 9593643.1427
15.8 | 1.0417 | 1.5 | 244 | 3.98 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.8 | 0.055556 | 0.08 | 245 | 3.628 | 16873.2 | 0.011799 | 2282064.5633 | 2480504.9601 | 0.4 | 800000 | 3456000 | 5936504.9601 | 5936504.9601
2.4 | 0.16667 | 0.24 | 246 | 3.436 | 50619.6 | 0.021595 | 3740548.2606 | 4065813.3267 | 1.2 | 2400000 | 3456000 | 7521813.3267 | 7521813.3267
0 | 0 | 0 | 247 | 3.004 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
1.6 | 0.11111 | 0.16 | 248 | 2.732 | 33746.4 | 0.017276 | 3117043.133 | 3388090.3619 | 0.8 | 1600000 | 3456000 | 6844090.3619 | 6844090.3619
0 | 0 | 0 | 249 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
29.6 | 1.0417 | 1.5 | 250 | 3.368 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
13 | 0.90278 | 1.3 | 251 | 4.236 | 274189.5 | 0.054771 | 7988593.9538 | 8683254.2976 | 6.5 | 13000000 | 3456000 | 12139254.2976 | 12139254.2976
1.4 | 0.097222 | 0.14 | 252 | 3.944 | 29528.1 | 0.016053 | 2935341.1941 | 3190588.2545 | 0.7 | 1400000 | 3456000 | 6646588.2545 | 6646588.2545
0 | 0 | 0 | 253 | 3.512 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 254 | 3.08 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 255 | 2.648 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 256 | 2.216 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 257 | 1.784 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
2 | 0.13889 | 0.2 | 258 | 1.552 | 42183 | 0.019533 | 3446101.0659 | 3745762.0281 | 1 | 2000000 | 3456000 | 7201762.0281 | 7201762.0281
4 | 0.27778 | 0.4 | 259 | 1.52 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
2.8 | 0.19444 | 0.28 | 260 | 1.368 | 59056.2 | 0.023507 | 4009008.791 | 4357618.2511 | 1.4 | 2800000 | 3456000 | 7813618.2511 | 7813618.2511
46.4 | 1.0417 | 1.5 | 261 | 2.436 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
86.8 | 1.0417 | 1.5 | 262 | 3.504 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
1.4 | 0.097222 | 0.14 | 263 | 3.212 | 29528.1 | 0.016053 | 2935341.1941 | 3190588.2545 | 0.7 | 1400000 | 3456000 | 6646588.2545 | 6646588.2545
4.2 | 0.29167 | 0.42 | 264 | 3.2 | 88584.3 | 0.029386 | 4810530.6705 | 5228837.6853 | 2.1 | 4200000 | 3456000 | 8684837.6853 | 8684837.6853
39.8 | 1.0417 | 1.5 | 265 | 4.268 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
29.8 | 1.0417 | 1.5 | 266 | 5.336 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
11.8 | 0.81944 | 1.18 | 267 | 6.084 | 248879.7 | 0.051921 | 7649194.4552 | 8314341.7991 | 5.9 | 11800000 | 3456000 | 11770341.7991 | 11770341.7991
1.6 | 0.11111 | 0.16 | 268 | 5.812 | 33746.4 | 0.017276 | 3117043.133 | 3388090.3619 | 0.8 | 1600000 | 3456000 | 6844090.3619 | 6844090.3619
0 | 0 | 0 | 269 | 5.38 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 270 | 4.948 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 271 | 4.516 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 272 | 4.084 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 273 | 3.652 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 274 | 3.22 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 275 | 2.788 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 276 | 2.356 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 277 | 1.924 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 278 | 1.492 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
4 | 0.27778 | 0.4 | 279 | 1.46 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
15.6 | 1.0417 | 1.5 | 280 | 2.528 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
9.2 | 0.63889 | 0.92 | 281 | 3.016 | 194041.8 | 0.045262 | 6841185.9025 | 7436071.6332 | 4.6 | 9200000 | 3456000 | 10892071.6332 | 10892071.6332
26.4 | 1.0417 | 1.5 | 282 | 4.084 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
27 | 1.0417 | 1.5 | 283 | 5.152 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
37.6 | 1.0417 | 1.5 | 284 | 6.22 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.8 | 0.055556 | 0.08 | 285 | 5.868 | 16873.2 | 0.011799 | 2282064.5633 | 2480504.9601 | 0.4 | 800000 | 3456000 | 5936504.9601 | 5936504.9601
0.6 | 0.041667 | 0.06 | 286 | 5.496 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
0 | 0 | 0 | 287 | 5.064 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 288 | 4.632 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
14.2 | 0.98611 | 1.42 | 289 | 5.62 | 299499.3 | 0.057506 | 8310987.5712 | 9033682.1426 | 7.1 | 14200000 | 3456000 | 12489682.1426 | 12489682.1426
6.4 | 0.44444 | 0.64 | 290 | 5.828 | 134985.6 | 0.037058 | 5812702.185 | 6318154.5489 | 3.2 | 6400000 | 3456000 | 9774154.5489 | 9774154.5489
23.4 | 1.0417 | 1.5 | 291 | 6.896 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0.6 | 0.041667 | 0.06 | 292 | 6.524 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
10.2 | 0.70833 | 1.02 | 293 | 7.112 | 215133.3 | 0.047912 | 7165329.2595 | 7788401.369 | 5.1 | 10200000 | 3456000 | 11244401.369 | 11244401.369
4 | 0.27778 | 0.4 | 294 | 7.08 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
9.8 | 0.68056 | 0.98 | 295 | 7.628 | 206696.7 | 0.046866 | 7037884.3647 | 7649874.3094 | 4.9 | 9800000 | 3456000 | 11105874.3094 | 11105874.3094
0 | 0 | 0 | 296 | 7.196 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
5.8 | 0.40278 | 0.58 | 297 | 7.344 | 122330.7 | 0.035102 | 5561297.8149 | 6044888.9292 | 2.9 | 5800000 | 3456000 | 9500888.9292 | 9500888.9292
4 | 0.27778 | 0.4 | 298 | 7.312 | 84366 | 0.028607 | 4706195.4447 | 5115429.8312 | 2 | 4000000 | 3456000 | 8571429.8312 | 8571429.8312
0 | 0 | 0 | 299 | 6.88 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
6.8 | 0.47222 | 0.68 | 300 | 7.128 | 143422.2 | 0.038316 | 5973127.4264 | 6492529.8113 | 3.4 | 6800000 | 3456000 | 9948529.8113 | 9948529.8113
39 | 1.0417 | 1.5 | 301 | 8.196 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
40.6 | 1.0417 | 1.5 | 302 | 9.264 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
35.4 | 1.0417 | 1.5 | 303 | 10.332 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
21.2 | 1.0417 | 1.5 | 304 | 11.4 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
1.2 | 0.083333 | 0.12 | 305 | 11.088 | 25309.8 | 0.014747 | 2738701.4233 | 2976849.3732 | 0.6 | 1200000 | 3456000 | 6432849.3732 | 6432849.3732
0 | 0 | 0 | 306 | 10.656 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 307 | 10.224 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
3.4 | 0.23611 | 0.34 | 308 | 10.132 | 71711.1 | 0.026158 | 4374666.4164 | 4755072.1918 | 1.7 | 3400000 | 3456000 | 8211072.1918 | 8211072.1918
6 | 0.41667 | 0.6 | 309 | 10.3 | 126549 | 0.035763 | 5646631.6913 | 6137643.1427 | 3 | 6000000 | 3456000 | 9593643.1427 | 9593643.1427
44.2 | 1.0417 | 1.5 | 310 | 11.368 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
2.2 | 0.15278 | 0.22 | 311 | 11.156 | 46401.3 | 0.020585 | 3597017.6124 | 3909801.7526 | 1.1 | 2200000 | 3456000 | 7365801.7526 | 7365801.7526
1.6 | 0.11111 | 0.16 | 312 | 10.884 | 33746.4 | 0.017276 | 3117043.133 | 3388090.3619 | 0.8 | 1600000 | 3456000 | 6844090.3619 | 6844090.3619
0 | 0 | 0 | 313 | 10.452 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
20.5 | 1.0417 | 1.5 | 314 | 11.52 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
18.8 | 1.0417 | 1.5 | 315 | 12.588 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
59 | 1.0417 | 1.5 | 316 | 13.656 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
11.4 | 0.79167 | 1.14 | 317 | 14.364 | 240443.1 | 0.050943 | 7531826.3883 | 8186767.8134 | 5.7 | 11400000 | 3456000 | 11642767.8134 | 11642767.8134
0.6 | 0.041667 | 0.06 | 318 | 13.992 | 12654.9 | 0.010072 | 2005015.1037 | 2179364.2432 | 0.3 | 600000 | 3456000 | 5635364.2432 | 5635364.2432
6 | 0.41667 | 0.6 | 319 | 14.16 | 126549 | 0.035763 | 5646631.6913 | 6137643.1427 | 3 | 6000000 | 3456000 | 9593643.1427 | 9593643.1427
55.4 | 1.0417 | 1.5 | 320 | 15.228 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
6.2 | 0.43056 | 0.62 | 321 | 15.416 | 130767.3 | 0.036415 | 5730407.4353 | 6228703.734 | 3.1 | 6200000 | 3456000 | 9684703.734 | 9684703.734
0 | 0 | 0 | 322 | 14.984 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 323 | 14.552 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 324 | 14.12 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 325 | 13.688 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 326 | 13.256 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 327 | 12.824 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 328 | 12.392 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 329 | 11.96 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 330 | 11.528 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 331 | 11.096 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 332 | 10.664 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 333 | 10.232 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
13 | 0.90278 | 1.3 | 334 | 11.1 | 274189.5 | 0.054771 | 7988593.9538 | 8683254.2976 | 6.5 | 13000000 | 3456000 | 12139254.2976 | 12139254.2976
34.6 | 1.0417 | 1.5 | 335 | 12.168 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
27.4 | 1.0417 | 1.5 | 336 | 13.236 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
32.6 | 1.0417 | 1.5 | 337 | 14.304 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
27.2 | 1.0417 | 1.5 | 338 | 15.372 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
33.8 | 1.0417 | 1.5 | 339 | 16.44 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
22.4 | 1.0417 | 1.5 | 340 | 17.508 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
37.2 | 1.0417 | 1.5 | 341 | 18.576 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
27 | 1.0417 | 1.5 | 342 | 19.644 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
4.8 | 0.33333 | 0.48 | 343 | 19.692 | 101239.2 | 0.031628 | 5108023.6078 | 5552199.5737 | 2.4 | 4800000 | 3456000 | 9008199.5737 | 9008199.5737
12.2 | 0.84722 | 1.22 | 344 | 20.48 | 257316.3 | 0.052885 | 7764373.2095 | 8439536.0973 | 6.1 | 12200000 | 3456000 | 11895536.0973 | 11895536.0973
3.4 | 0.23611 | 0.34 | 345 | 20.388 | 71711.1 | 0.026158 | 4374666.4164 | 4755072.1918 | 1.7 | 3400000 | 3456000 | 8211072.1918 | 8211072.1918
23.8 | 1.0417 | 1.5 | 346 | 21.456 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
0 | 0 | 0 | 347 | 21.024 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
2.4 | 0.16667 | 0.24 | 348 | 20.832 | 50619.6 | 0.021595 | 3740548.2606 | 4065813.3267 | 1.2 | 2400000 | 3456000 | 7521813.3267 | 7521813.3267
3 | 0.20833 | 0.3 | 349 | 20.7 | 63274.5 | 0.024417 | 4135312.2152 | 4494904.5817 | 1.5 | 3000000 | 3456000 | 7950904.5817 | 7950904.5817
2.2 | 0.15278 | 0.22 | 350 | 20.488 | 46401.3 | 0.020585 | 3597017.6124 | 3909801.7526 | 1.1 | 2200000 | 3456000 | 7365801.7526 | 7365801.7526
21.8 | 1.0417 | 1.5 | 351 | 21.556 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
25.5 | 1.0417 | 1.5 | 352 | 22.624 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
31.8 | 1.0417 | 1.5 | 353 | 23.692 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
22.6 | 1.0417 | 1.5 | 354 | 24.76 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
9 | 0.625 | 0.9 | 355 | 25.228 | 189823.5 | 0.044717 | 6774046.2561 | 7363093.7566 | 4.5 | 9000000 | 3456000 | 10819093.7566 | 10819093.7566
35.8 | 1.0417 | 1.5 | 356 | 26.296 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
9.4 | 0.65278 | 0.94 | 357 | 26.804 | 198260.1 | 0.045802 | 6907521.4948 | 7508175.5379 | 4.7 | 9400000 | 3456000 | 10964175.5379 | 10964175.5379
0 | 0 | 0 | 358 | 26.372 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 359 | 25.94 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
26.2 | 1.0417 | 1.5 | 360 | 27.008 | 316372.5 | 0.059273 | 8517561.9968 | 9258219.5618 | 7.5 | 15000000 | 3456000 | 12714219.5618 | 12714219.5618
1.6 | 0.11111 | 0.16 | 361 | 26.736 | 33746.4 | 0.017276 | 3117043.133 | 3388090.3619 | 0.8 | 1600000 | 3456000 | 6844090.3619 | 6844090.3619
0.2 | 0.013889 | 0.02 | 362 | 26.324 | 4218.3 | 0.0055039 | 1223030.7852 | 1329381.2883 | 0.1 | 200000 | 3456000 | 4785381.2883 | 4785381.2883
0 | 0 | 0 | 363 | 25.892 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 364 | 25.46 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000
0 | 0 | 0 | 365 | 25.028 | 0 | 0 | 0 | 0 | 0 | 0 | 3456000 | 3456000 | 3456000

## Rainfall Data
Date | Daily Rainfall 1 (2014) | Daily Rainfall (mm) (2015) | Daily Rainfall (mm) (Station 2) | Daily Rainfall (mm) (Station 3)
[-] | [mm] | 7.8 | 0 | 0
2014-01-01 | 18.8 | 1 | 1.4 | 0
2014-01-02 | 19.8 | 13.4 | 7.8 | 0
2014-01-03 | 0 | 64.2 | 29.6 | 0
2014-01-04 | 0 | 32.2 | 6 | 4.4
2014-01-05 | 0 | 2.8 | 0 | 5.6
2014-01-06 | 5 | 0 | 0 | 5
2014-01-07 | 20.4 | 0 | 0 | 2.6
2014-01-08 | 24.8 | 0.8 | 1 | 0.2
2014-01-09 | 34 | 0 | 0.6 | 0
2014-01-10 | 44.6 | 0 | 1.6 | 0
2014-01-11 | 14.4 | 0 | 0 | 0
2014-01-12 | 50.2 | 0 | 0 | 0
2014-01-13 | 9.6 | 0.4 | 0 | 0
2014-01-14 | 5.8 | 35.4 | 12.4 | 1
2014-01-15 | 1.6 | 6 | 1.6 | 1.2
2014-01-16 | 0.8 | 20.4 | 28.8 | 2.2
2014-01-17 | 0 | 16.6 | 1 | 0
2014-01-18 | 2.6 | 2.6 | 0 | 0
2014-01-19 | 1 | 0.4 | 0 | 0
2014-01-20 | 0.6 | 18.4 | 7.2 | 0
2014-01-21 | 0.8 | 14 | 5.2 | 0.2
2014-01-22 | 0.6 | 90.8 | 5.6 | 6.4
2014-01-23 | 0 | 40 | 6.6 | 2.2
2014-01-24 | 0 | 1.8 | 0 | 0.2
2014-01-25 | 0 | 2.8 | 0 | 1.6
2014-01-26 | 0 | 2.8 | 0.6 | 4.6
2014-01-27 | 17.6 | 0 | 0 | 10.4
2014-01-28 | 0 | 0 | 0 | 10.8
2014-01-29 | 0 | 0.6 | 0 | 6.2
2014-01-30 | 0 | 5.8 | 1.2 | 1.4
2014-01-31 | 2.6 | 8 | 1.8 | 0
2014-02-01 | 2.6 | 27 | 4 | 1
2014-02-02 | 0 | 0.6 | 1.4 | 8
2014-02-03 | 0 | 36 | 17 | 1.6
2014-02-04 | 0 | 27.2 | 39.6 | 3.8
2014-02-05 | 0 | 28.2 | 9.8 | 0.2
2014-02-06 | 0 | 39.2 | 11.4 | 1.6
2014-02-07 | 0 | 6.6 | 13.2 | 0.2
2014-02-08 | 0 | 3.2 | 11.8 | 0
2014-02-09 | 12.2 | 0.2 | 0.8 | 1
2014-02-10 | 13.4 | 19.6 | 1 | 1.4
2014-02-11 | 46.6 | 30.4 | 12.8 | 4.6
2014-02-12 | 16.8 | 19 | 16.2 | 3
2014-02-13 | 15.6 | 0.2 | 0 | 5.6
2014-02-14 | 3 | 0 | 0 | 2.4
2014-02-15 | 11.6 | 0 | 0 | 0
2014-02-16 | 19 | 0 | 0 | 0
2014-02-17 | 9.2 | 4 | 0 | 0
2014-02-18 | 12.6 | 11 | 0 | 0
2014-02-19 | 21.8 | 0.4 | 0 | 2.2
2014-02-20 | 2.4 | 0 | 0 | 9
2014-02-21 | 0.8 | 0 | 0 | 10.6
2014-02-22 | 4.8 | 0 | 0 | 4.6
2014-02-23 | 14.6 | 0.2 | 0 | 23.6
2014-02-24 | 6.8 | 4.6 | 1.6 | 1.6
2014-02-25 | 0 | 8.8 | 8.2 | 2.2
2014-02-26 | 0.8 | 0.4 | 0 | 0.2
2014-02-27 | 0 | 0 | 0 | 8.6
2014-02-28 | 0.4 | 1.2 | 2.2 | 20
2014-03-01 | 2 | 0 | 0 | 4.4
2014-03-02 | 19 | 0 | 0 | 0
2014-03-03 | 1 | 0.4 | 0 | 0
2014-03-04 | 2.4 | 1.8 | 0 | 0
2014-03-05 | 23.8 | 0.8 | 0 | 0
2014-03-06 | 8.6 | 0 | 0 | 0
2014-03-07 | 34 | 0.4 | 0 | 0
2014-03-08 | 52.4 | 0.4 | 0 | 0.8
2014-03-09 | 10.6 | 2.8 | 0.8 | 0
2014-03-10 | 2.4 | 13.6 | 6.4 | 4
2014-03-11 | 0 | 8.6 | 0.8 | 22.8
2014-03-12 | 2.8 | 17.4 | 8.4 | 25.2
2014-03-13 | 20.2 | 0.6 | 1 | 5.6
2014-03-14 | 13.8 | 0 | 0 | 1.4
2014-03-15 | 22.8 | 0 | 0 | 0
2014-03-16 | 5.4 | 0 | 0 | 1.8
2014-03-17 | 0.4 | 31 | 7.4 | 0
2014-03-18 | 31 | 35.4 | 10 | 7.6
2014-03-19 | 1.6 | 28.6 | 15.2 | 3
2014-03-20 | 1.6 | 0 | 0.2 | 0
2014-03-21 | 7.6 | 7 | 4.4 | 0
2014-03-22 | 2.6 | 9.6 | 8.2 | 0
2014-03-23 | 0 | 18.2 | 11.8 | 0
2014-03-24 | 4 | 104.4 | 5.4 | 0.4
2014-03-25 | 31 | 33.2 | 0 | 0.8
2014-03-26 | 0.2 | 26.2 | 12.8 | 0
2014-03-27 | 4.4 | 68.8 | 4.6 | 0
2014-03-28 | 23.6 | 10 | 11.8 | 0
2014-03-29 | 41.6 | 37.7 | 22 | 0
2014-03-30 | 3 | 11.6 | 2 | 0
2014-03-31 | 0 | 0 | 0 | 0
2014-04-01 | 0 | 33.7 | 0.4 | 0
2014-04-02 | 5.6 | 9 | 6.2 | 0
2014-04-03 | 20.4 | 8.4 | 1.4 | 9.8
2014-04-04 | 2.6 | 0.6 | 0 | 2.2
2014-04-05 | 15.9 | 0 | 0 | 3.4
2014-04-06 | 9.4 | 0 | 0 | 0
2014-04-07 | 13.6 | 0 | 0 | 2
2014-04-08 | 5.6 | 3.2 | 0 | 0
2014-04-09 | 0 | 40.2 | 3.4 | 1.2
2014-04-10 | 16.6 | 9.2 | 2.2 | 1
2014-04-11 | 0 | 24.4 | 5 | 8.4
2014-04-12 | 0 | 16.2 | 9.2 | 0
2014-04-13 | 0 | 1.5 | 0 | 0
2014-04-14 | 14.8 | 37.2 | 0 | 0
2014-04-15 | 20.8 | 3 | 0 | 0
2014-04-16 | 37.4 | 0 | 0 | 0
2014-04-17 | 9.8 | 0 | 0 | 8.2
2014-04-18 | 1.9 | 0 | 0 | 0.8
2014-04-19 | 21 | 1.1 | 0 | 0
2014-04-20 | 30 | 0.4 | 5 | 0
2014-04-21 | 0 | 8.2 | 0.8 | 0
2014-04-22 | 4.4 | 8.4 | 22.2 | 0
2014-04-23 | 12.8 | 1.8 | 6.8 | 0.6
2014-04-24 | 26 | 0 | 0.6 | 1.2
2014-04-25 | 1.8 | 4.2 | 0.4 | 18.6
2014-04-26 | 35 | 22.4 | 1.2 | 2.8
2014-04-27 | 7.2 | 15.4 | 0.8 | 7
2014-04-28 | 0.8 | 27.6 | 0 | 0
2014-04-29 | 0.1 | 4.8 | 1.6 | 0.2
2014-04-30 | 0 | 0.8 | 0 | 0.2
2014-05-01 | 0 | 0 | 0 | 1
2014-05-02 | 2 | 0 | 0 | 0
2014-05-03 | 4.6 | 19.8 | 0.4 | 0
2014-05-04 | 3.8 | 0.4 | 1.6 | 0
2014-05-05 | 0 | 0 | 0 | 0
2014-05-06 | 0 | 0 | 0 | 0
2014-05-07 | 0 | 0 | 0 | 0
2014-05-08 | 0 | 0 | 0 | 0
2014-05-09 | 0 | 0.4 | 0 | 0
2014-05-10 | 0.2 | 0 | 0 | 21.8
2014-05-11 | 0 | 0 | 9.4 | 9.1
2014-05-12 | 0.2 | 0 | 2.2 | 1
2014-05-13 | 0 | 0 | 0.4 | 2.6
2014-05-14 | 0 | 0 | 0 | 1.2
2014-05-15 | 0 | 0.2 | 0 | 0
2014-05-16 | 2.8 | 0 | 0 | 0.4
2014-05-17 | 0 | 0 | 0 | 1.6
2014-05-18 | 0 | 0 | 0 | 0
2014-05-19 | 0 | 0 | 0 | 2.8
2014-05-20 | 0 | 0 | 0 | 3.6
2014-05-21 | 8.2 | 0.2 | 0 | 0.4
2014-05-22 | 29.6 | 0.2 | 0 | 9.4
2014-05-23 | 0.8 | 0 | 0 | 1.4
2014-05-24 | 5.2 | 0 | 0 | 1.2
2014-05-25 | 23.4 | 0 | 0 | 2.2
2014-05-26 | 0 | 0 | 0 | 0.8
2014-05-27 | 4.4 | 0 | 0 | 0.4
2014-05-28 | 0 | 0 | 0 | 2.4
2014-05-29 | 0 | 0 | 0 | 3.6
2014-05-30 | 0 | 0 | 0 | 0.2
2014-05-31 | 0 | 7.4 | 5.8 | 0.6
2014-06-01 | 0 | 2.8 | 9.2 | 0
2014-06-02 | 0 | 0 | 0 | 0
2014-06-03 | 0 | 0 | 0 | 0.4
2014-06-04 | 0 | 0 | 0 | 0
2014-06-05 | 0 | 0 | 0 | 11.4
2014-06-06 | 0 | 0 | 0 | 1.6
2014-06-07 | 0 | 0 | 0 | 2.8
2014-06-08 | 0.2 | 0 | 0 | 0.6
2014-06-09 | 0 | 0 | 0 | 1.2
2014-06-10 | 0 | 0 | 0 | 19.6
2014-06-11 | 0 | 0 | 0 | 7.4
2014-06-12 | 0 | 0 | 0 | 0.2
2014-06-13 | 0 | 0 | 0 | 0
2014-06-14 | 3.6 | 0 | 0 | 1.2
2014-06-15 | 0 | 0 | 0 | 0.4
2014-06-16 | 0 | 0 | 0 | 2.4
2014-06-17 | 0 | 7 | 1.6 | 1.8
2014-06-18 | 1.6 | 0 | 0.4 | 6.8
2014-06-19 | 20.8 | 0 | 0 | 5.4
2014-06-20 | 3.2 | 0 | 0 | 0
2014-06-21 | 1.2 | 0 | 0 | 0
2014-06-22 | 0 | 1.4 | 0 | 0.8
2014-06-23 | 15.4 | 13.4 | 0 | 7
2014-06-24 | 1.2 | 4 | 0 | 0
2014-06-25 | 0 | 0 | 0 | 1.4
2014-06-26 | 5.8 | 0 | 0 | 2
2014-06-27 | 20.4 | 0 | 0 | 3.4
2014-06-28 | 20.4 | 0 | 0 | 0
2014-06-29 | 0.6 | 0 | 0 | 0
2014-06-30 | 0 | 0 | 0 | 1.6
2014-07-01 | 0 | 0 | 0 | 0.2
2014-07-02 | 1.8 | 0 | 0 | 0
2014-07-03 | 6.2 | 0 | 0 | 0
2014-07-04 | 9.4 | 0 | 0 | 0
2014-07-05 | 26.6 | 0 | 0 | 0
2014-07-06 | 13.6 | 0.2 | 0 | 0
2014-07-07 | 0 | 0 | 0 | 0.6
2014-07-08 | 0 | 1 | 0 | 0.2
2014-07-09 | 0 | 1.2 | 0 | 3.4
2014-07-10 | 0 | 2.4 | 10.8 | 2.8
2014-07-11 | 0 | 4 | 12 | 0.2
2014-07-12 | 0 | 0 | 0 | 2.2
2014-07-13 | 0 | 0 | 0 | 1.4
2014-07-14 | 0 | 0 | 0 | 0
2014-07-15 | 0 | 0 | 0 | 0
2014-07-16 | 0 | 0 | 0 | 0
2014-07-17 | 0 | 0 | 0 | 0
2014-07-18 | 37 | 0 | 0 | 0
2014-07-19 | 1.8 | 0.6 | 0 | 0
2014-07-20 | 0 | 0 | 0 | 0
2014-07-21 | 0 | 0 | 0 | 0
2014-07-22 | 8 | 8.4 | 0.4 | 0
2014-07-23 | 18.2 | 4 | 1 | 0
2014-07-24 | 0.6 | 4.2 | 10.8 | 0
2014-07-25 | 0 | 0 | 0.6 | 0
2014-07-26 | 0 | 0 | 0 | 0
2014-07-27 | 0 | 0 | 0 | 0
2014-07-28 | 0 | 0 | 0 | 0
2014-07-29 | 0 | 0 | 0 | 0
2014-07-30 | 0 | 0 | 0 | 5.4
2014-07-31 | 0 | 0 | 0 | 0.4
2014-08-01 | 0 | 0 | 0 | 0
2014-08-02 | 0 | 0 | 0 | 0
2014-08-03 | 0 | 0 | 6.6 | 0
2014-08-04 | 0 | 0 | 4.8 | 0
2014-08-05 | 0 | 3.2 | 0 | 0
2014-08-06 | 0 | 14.6 | 0.2 | 0
2014-08-07 | 0 | 24.4 | 5 | 0
2014-08-08 | 0 | 1.8 | 1 | 0
2014-08-09 | 0 | 0 | 0 | 0
2014-08-10 | 0 | 0 | 0 | 0.4
2014-08-11 | 0 | 0 | 0 | 4.4
2014-08-12 | 0 | 0 | 0 | 1
2014-08-13 | 0 | 0 | 9.8 | 0.4
2014-08-14 | 0 | 0 | 3 | 8.4
2014-08-15 | 0 | 0 | 0 | 4.4
2014-08-16 | 0 | 0 | 0 | 4.4
2014-08-17 | 0 | 0 | 0 | 14.8
2014-08-18 | 0 | 0 | 0 | 5.6
2014-08-19 | 0 | 0 | 0 | 1.2
2014-08-20 | 0 | 0 | 0 | 0.4
2014-08-21 | 0 | 0 | 0 | 0.6
2014-08-22 | 0 | 0 | 0 | 5.2
2014-08-23 | 0 | 0 | 0 | 1.4
2014-08-24 | 0 | 0 | 0 | 0
2014-08-25 | 0 | 0 | 0 | 0
2014-08-26 | 0 | 2.8 | 3 | 0.4
2014-08-27 | 0 | 10.4 | 6.8 | 1.2
2014-08-28 | 0.4 | 33.4 | 16.2 | 4
2014-08-29 | 7.8 | 26 | 6.2 | 0
2014-08-30 | 3.6 | 6 | 14.2 | 0
2014-08-31 | 10.6 | 15.8 | 1.6 | 0
2014-09-01 | 3.2 | 0.8 | 9.4 | 0
2014-09-02 | 6.2 | 2.4 | 0.6 | 4.8
2014-09-03 | 0 | 0 | 0 | 0
2014-09-04 | 0 | 1.6 | 0.2 | 0
2014-09-05 | 0 | 0 | 0.2 | 0
2014-09-06 | 0 | 29.6 | 4 | 0
2014-09-07 | 0 | 13 | 0 | 0
2014-09-08 | 0 | 1.4 | 0 | 0
2014-09-09 | 0 | 0 | 0 | 0
2014-09-10 | 0 | 0 | 0 | 0
2014-09-11 | 0 | 0 | 0 | 0
2014-09-12 | 0 | 0 | 0 | 0
2014-09-13 | 0 | 0 | 0 | 0
2014-09-14 | 0 | 2 | 3.2 | 0.6
2014-09-15 | 0 | 4 | 6.4 | 0
2014-09-16 | 0 | 2.8 | 2 | 0.8
2014-09-17 | 0 | 46.4 | 8.6 | 1.2
2014-09-18 | 26.4 | 86.8 | 9.8 | 0.8
2014-09-19 | 0.4 | 1.4 | 7.4 | 1.4
2014-09-20 | 0 | 4.2 | 0 | 1.4
2014-09-21 | 2 | 39.8 | 0 | 5
2014-09-22 | 12.4 | 29.8 | 8.4 | 1.2
2014-09-23 | 29.4 | 11.8 | 7.8 | 1.6
2014-09-24 | 1.6 | 1.6 | 0.4 | 0
2014-09-25 | 0.6 | 0 | 0 | 4
2014-09-26 | 8.2 | 0 | 0 | 1.6
2014-09-27 | 0 | 0 | 0 | 11
2014-09-28 | 12.4 | 0 | 0 | 5
2014-09-29 | 5.6 | 0 | 0 | 2.2
2014-09-30 | 0 | 0 | 0 | 0
2014-10-01 | 0 | 0 | 0 | 0
2014-10-02 | 0 | 0 | 0 | 1.2
2014-10-03 | 57.8 | 0 | 0 | 28.4
2014-10-04 | 6 | 0 | 0 | 26
2014-10-05 | 9.2 | 4 | 2.4 | 8.8
2014-10-06 | 0.4 | 15.6 | 9 | 10.6
2014-10-07 | 0 | 9.2 | 1 | 0
2014-10-08 | 1.4 | 26.4 | 15.6 | 1.2
2014-10-09 | 1.8 | 27 | 14.4 | 0
2014-10-10 | 17.8 | 37.6 | 7.8 | 0
2014-10-11 | 15.4 | 0.8 | 6 | 0
2014-10-12 | 33 | 0.6 | 0 | 0
2014-10-13 | 31.4 | 0 | 0 | 0
2014-10-14 | 28.4 | 0 | 0 | 1
2014-10-15 | 6.4 | 14.2 | 4.8 | 0
2014-10-16 | 17.2 | 6.4 | 1.8 | 0
2014-10-17 | 27 | 23.4 | 3.2 | 0
2014-10-18 | 16.8 | 0.6 | 4.2 | 0
2014-10-19 | 46.2 | 10.2 | 0 | 0
2014-10-20 | 10.8 | 4 | 6 | 0
2014-10-21 | 40.2 | 9.8 | 0 | 0
2014-10-22 | 21.4 | 0 | 0 | 0
2014-10-23 | 9.4 | 5.8 | 0.8 | 0
2014-10-24 | 1.6 | 4 | 0 | 0
2014-10-25 | 21.8 | 0 | 0 | 9.6
2014-10-26 | 2.4 | 6.8 | 6 | 0
2014-10-27 | 33.6 | 39 | 4.8 | 0
2014-10-28 | 24.4 | 40.6 | 10.2 | 0
2014-10-29 | 7 | 35.4 | 8 | 14.1
2014-10-30 | 9 | 21.2 | 10 | 2
2014-10-31 | 15 | 1.2 | 7.6 | 0.8
2014-11-01 | 6.4 | 0 | 0 | 0
2014-11-02 | 37.6 | 0 | 0 | 0
2014-11-03 | 35.2 | 3.4 | 4.6 | 1.2
2014-11-04 | 9 | 6 | 2 | 3
2014-11-05 | 4.4 | 44.2 | 15 | 3.2
2014-11-06 | 20.2 | 2.2 | 3.6 | 3.2
2014-11-07 | 1.4 | 1.6 | 4.4 | 5.6
2014-11-08 | 34 | 0 | 0 | 0
2014-11-09 | 0 | 20.5 | 9.6 | 0
2014-11-10 | 0 | 18.8 | 1.2 | 1.8
2014-11-11 | 0 | 59 | 8.2 | 9.6
2014-11-12 | 0 | 11.4 | 0.8 | 8.8
2014-11-13 | 0 | 0.6 | 2.4 | 1.4
2014-11-14 | 0 | 6 | 0.2 | 11.8
2014-11-15 | 0 | 55.4 | 8.2 | 0
2014-11-16 | 0 | 6.2 | 5.8 | 4.6
2014-11-17 | 0 | 0 | 0 | 0
2014-11-18 | 0 | 0 | 0 | 0
2014-11-19 | 3.4 | 0 | 0 | 0
2014-11-20 | 29.4 | 0 | 0 | 0.6
2014-11-21 | 32.8 | 0 | 1.8 | 0
2014-11-22 | 25.6 | 0 | 4.6 | 5
2014-11-23 | 15.2 | 0 | 0 | 4.4
2014-11-24 | 60.6 | 0 | 0 | 0
2014-11-25 | 15 | 0 | 0 | 0.2
2014-11-26 | 43 | 0 | 0 | 3.6
2014-11-27 | 15 | 0 | 0 | 2.4
2014-11-28 | 0 | 0 | 0 | 10.2
2014-11-29 | 0 | 13 | 4 | 26.6
2014-11-30 | 0 | 34.6 | 8.4 | 5.4
2014-12-01 | 0 | 27.4 | 39.2 | 0
2014-12-02 | 0 | 32.6 | 10.2 | 0
2014-12-03 | 0 | 27.2 | 6.4 | 0
2014-12-04 | 1.2 | 33.8 | 48.2 | 0
2014-12-05 | 45.4 | 22.4 | 16.8 | 0
2014-12-06 | 0.8 | 37.2 | 11 | 0
2014-12-07 | 15.2 | 27 | 11 | 0
2014-12-08 | 48.6 | 4.8 | 3.2 | 0
2014-12-09 | 34.2 | 12.2 | 9 | 0
2014-12-10 | 4.4 | 3.4 | 3 | 3.2
2014-12-11 | 17.8 | 23.8 | 35.2 | 1.8
2014-12-12 | 1.4 | 0 | 1 | 10.4
2014-12-13 | 1 | 2.4 | 0 | 26
2014-12-14 | 0 | 3 | 2 | 0.8
2014-12-15 | 9 | 2.2 | 0 | 11.8
2014-12-16 | 20.2 | 21.8 | 10.2 | 4.6
2014-12-17 | 0.8 | 25.5 | 5.4 | 0
2014-12-18 | 24.6 | 31.8 | 11.4 | 0
2014-12-19 | 0 | 22.6 | 2.4 | 3.8
2014-12-20 | 0 | 9 | 0.4 | 7.6
2014-12-21 | 8.8 | 35.8 | 4 | 20.6
2014-12-22 | 11.6 | 9.4 | 10.8 | 1.4
2014-12-23 | 10 | 0 | 0.6 | 3.8
2014-12-24 | 2.2 | 0 | 0 | 25.6
2014-12-25 | 0.6 | 26.2 | 6.4 | 24.8
2014-12-26 | 10.2 | 1.6 | 2.4 | 2.2
2014-12-27 | 5.4 | 0.2 | 0 | 21.8
2014-12-28 | 0 | 0 | 0 | 2.4
2014-12-29 | 0 | 0 | 0 | 2.8
2014-12-30 | 0 | 0 | 0 | 0.2
2014-12-31 | 0

## Chlorine Filter (2)
Contact Time | 10 | min |  | Chlorine Total |  | Maintainence Total | COSTS
Solution Concentration | 5 | % |  | 23172.6667 | g | 7 | Initial Cost | 700 | $
CT_Chlorine | 100 | mg * min / L |  | 23.1727 | Kg |  | Maintainence Cost | 100 | $
Refill Amount | 3 | Kg
| Q_in | Q_in | Chlorine Mass | Mass Total | Counter
| [L/min] | L / Day | [g] | [g]
1 | 0.54167 | 780 | 156 | 156
2 | 0.069444 | 69.4444 | 13.8889 | 169.8889
3 | 0.93056 | 930.5556 | 186.1111 | 356
4 | 1.0417 | 1041.6667 | 208.3333 | 564.3333
5 | 1.0417 | 1041.6667 | 208.3333 | 772.6667
6 | 0.19444 | 194.4444 | 38.8889 | 811.5556
7 | 0 | 0 | 0 | 811.5556
8 | 0 | 0 | 0 | 811.5556
9 | 0.055556 | 55.5556 | 11.1111 | 822.6667
10 | 0 | 0 | 0 | 822.6667
11 | 0 | 0 | 0 | 822.6667
12 | 0 | 0 | 0 | 822.6667
13 | 0 | 0 | 0 | 822.6667
14 | 0.027778 | 27.7778 | 5.5556 | 828.2222
15 | 1.0417 | 1041.6667 | 208.3333 | 1036.5556
16 | 0.41667 | 416.6667 | 83.3333 | 1119.8889
17 | 1.0417 | 1041.6667 | 208.3333 | 1328.2222
18 | 1.0417 | 1041.6667 | 208.3333 | 1536.5556
19 | 0.18056 | 180.5556 | 36.1111 | 1572.6667
20 | 0.027778 | 27.7778 | 5.5556 | 1578.2222
21 | 1.0417 | 1041.6667 | 208.3333 | 1786.5556
22 | 0.97222 | 972.2222 | 194.4444 | 1981
23 | 1.0417 | 1041.6667 | 208.3333 | 2189.3333
24 | 1.0417 | 1041.6667 | 208.3333 | 2397.6667
25 | 0.125 | 125 | 25 | 2422.6667
26 | 0.19444 | 194.4444 | 38.8889 | 2461.5556
27 | 0.19444 | 194.4444 | 38.8889 | 2500.4444
28 | 0 | 0 | 0 | 2500.4444
29 | 0 | 0 | 0 | 2500.4444
30 | 0.041667 | 41.6667 | 8.3333 | 2508.7778
31 | 0.40278 | 402.7778 | 80.5556 | 2589.3333
32 | 0.55556 | 555.5556 | 111.1111 | 2700.4444
33 | 1.0417 | 1041.6667 | 208.3333 | 2908.7778
34 | 0.041667 | 41.6667 | 8.3333 | 2917.1111
35 | 1.0417 | 1041.6667 | 208.3333 | 208.3333 | 1
36 | 1.0417 | 1041.6667 | 208.3333 | 416.6667
37 | 1.0417 | 1041.6667 | 208.3333 | 625
38 | 1.0417 | 1041.6667 | 208.3333 | 833.3333
39 | 0.45833 | 458.3333 | 91.6667 | 925
40 | 0.22222 | 222.2222 | 44.4444 | 969.4444
41 | 0.013889 | 13.8889 | 2.7778 | 972.2222
42 | 1.0417 | 1041.6667 | 208.3333 | 1180.5556
43 | 1.0417 | 1041.6667 | 208.3333 | 1388.8889
44 | 1.0417 | 1041.6667 | 208.3333 | 1597.2222
45 | 0.013889 | 13.8889 | 2.7778 | 1600
46 | 0 | 0 | 0 | 1600
47 | 0 | 0 | 0 | 1600
48 | 0 | 0 | 0 | 1600
49 | 0.27778 | 277.7778 | 55.5556 | 1655.5556
50 | 0.76389 | 763.8889 | 152.7778 | 1808.3333
51 | 0.027778 | 27.7778 | 5.5556 | 1813.8889
52 | 0 | 0 | 0 | 1813.8889
53 | 0 | 0 | 0 | 1813.8889
54 | 0 | 0 | 0 | 1813.8889
55 | 0.013889 | 13.8889 | 2.7778 | 1816.6667
56 | 0.31944 | 319.4444 | 63.8889 | 1880.5556
57 | 0.61111 | 611.1111 | 122.2222 | 2002.7778
58 | 0.027778 | 27.7778 | 5.5556 | 2008.3333
59 | 0 | 0 | 0 | 2008.3333
60 | 0.083333 | 83.3333 | 16.6667 | 2025
61 | 0 | 0 | 0 | 2025
62 | 0 | 0 | 0 | 2025
63 | 0.027778 | 27.7778 | 5.5556 | 2030.5556
64 | 0.125 | 125 | 25 | 2055.5556
65 | 0.055556 | 55.5556 | 11.1111 | 2066.6667
66 | 0 | 0 | 0 | 2066.6667
67 | 0.027778 | 27.7778 | 5.5556 | 2072.2222
68 | 0.027778 | 27.7778 | 5.5556 | 2077.7778
69 | 0.19444 | 194.4444 | 38.8889 | 2116.6667
70 | 0.94444 | 944.4444 | 188.8889 | 2305.5556
71 | 0.59722 | 597.2222 | 119.4444 | 2425
72 | 1.0417 | 1041.6667 | 208.3333 | 2633.3333
73 | 0.041667 | 41.6667 | 8.3333 | 2641.6667
74 | 0 | 0 | 0 | 2641.6667
75 | 0 | 0 | 0 | 2641.6667
76 | 0 | 0 | 0 | 2641.6667
77 | 1.0417 | 1041.6667 | 208.3333 | 2850
78 | 1.0417 | 1041.6667 | 208.3333 | 58.3333 | 1
79 | 1.0417 | 1041.6667 | 208.3333 | 266.6667
80 | 0 | 0 | 0 | 266.6667
81 | 0.48611 | 486.1111 | 97.2222 | 363.8889
82 | 0.66667 | 666.6667 | 133.3333 | 497.2222
83 | 1.0417 | 1041.6667 | 208.3333 | 705.5556
84 | 1.0417 | 1041.6667 | 208.3333 | 913.8889
85 | 1.0417 | 1041.6667 | 208.3333 | 1122.2222
86 | 1.0417 | 1041.6667 | 208.3333 | 1330.5556
87 | 1.0417 | 1041.6667 | 208.3333 | 1538.8889
88 | 0.69444 | 694.4444 | 138.8889 | 1677.7778
89 | 1.0417 | 1041.6667 | 208.3333 | 1886.1111
90 | 0.80556 | 805.5556 | 161.1111 | 2047.2222
91 | 0 | 0 | 0 | 2047.2222
92 | 1.0417 | 1041.6667 | 208.3333 | 2255.5556
93 | 0.625 | 625 | 125 | 2380.5556
94 | 0.58333 | 583.3333 | 116.6667 | 2497.2222
95 | 0.041667 | 41.6667 | 8.3333 | 2505.5556
96 | 0 | 0 | 0 | 2505.5556
97 | 0 | 0 | 0 | 2505.5556
98 | 0 | 0 | 0 | 2505.5556
99 | 0.22222 | 222.2222 | 44.4444 | 2550
100 | 1.0417 | 1041.6667 | 208.3333 | 2758.3333
101 | 0.63889 | 638.8889 | 127.7778 | 2886.1111
102 | 1.0417 | 1041.6667 | 208.3333 | 94.4444 | 1
103 | 1.0417 | 1041.6667 | 208.3333 | 302.7778
104 | 0.10417 | 104.1667 | 20.8333 | 323.6111
105 | 1.0417 | 1041.6667 | 208.3333 | 531.9444
106 | 0.20833 | 208.3333 | 41.6667 | 573.6111
107 | 0 | 0 | 0 | 573.6111
108 | 0 | 0 | 0 | 573.6111
109 | 0 | 0 | 0 | 573.6111
110 | 0.076389 | 76.3889 | 15.2778 | 588.8889
111 | 0.027778 | 27.7778 | 5.5556 | 594.4444
112 | 0.56944 | 569.4444 | 113.8889 | 708.3333
113 | 0.58333 | 583.3333 | 116.6667 | 825
114 | 0.125 | 125 | 25 | 850
115 | 0 | 0 | 0 | 850
116 | 0.29167 | 291.6667 | 58.3333 | 908.3333
117 | 1.0417 | 1041.6667 | 208.3333 | 1116.6667
118 | 1.0417 | 1041.6667 | 208.3333 | 1325
119 | 1.0417 | 1041.6667 | 208.3333 | 1533.3333
120 | 0.33333 | 333.3333 | 66.6667 | 1600
121 | 0.055556 | 55.5556 | 11.1111 | 1611.1111
122 | 0 | 0 | 0 | 1611.1111
123 | 0 | 0 | 0 | 1611.1111
124 | 1.0417 | 1041.6667 | 208.3333 | 1819.4444
125 | 0.027778 | 27.7778 | 5.5556 | 1825
126 | 0 | 0 | 0 | 1825
127 | 0 | 0 | 0 | 1825
128 | 0 | 0 | 0 | 1825
129 | 0 | 0 | 0 | 1825
130 | 0.027778 | 27.7778 | 5.5556 | 1830.5556
131 | 0 | 0 | 0 | 1830.5556
132 | 0 | 0 | 0 | 1830.5556
133 | 0 | 0 | 0 | 1830.5556
134 | 0 | 0 | 0 | 1830.5556
135 | 0 | 0 | 0 | 1830.5556
136 | 0.013889 | 13.8889 | 2.7778 | 1833.3333
137 | 0 | 0 | 0 | 1833.3333
138 | 0 | 0 | 0 | 1833.3333
139 | 0 | 0 | 0 | 1833.3333
140 | 0 | 0 | 0 | 1833.3333
141 | 0 | 0 | 0 | 1833.3333
142 | 0.013889 | 13.8889 | 2.7778 | 1836.1111
143 | 0.013889 | 13.8889 | 2.7778 | 1838.8889
144 | 0 | 0 | 0 | 1838.8889
145 | 0 | 0 | 0 | 1838.8889
146 | 0 | 0 | 0 | 1838.8889
147 | 0 | 0 | 0 | 1838.8889
148 | 0 | 0 | 0 | 1838.8889
149 | 0 | 0 | 0 | 1838.8889
150 | 0 | 0 | 0 | 1838.8889
151 | 0 | 0 | 0 | 1838.8889
152 | 0.51389 | 513.8889 | 102.7778 | 1941.6667
153 | 0.19444 | 194.4444 | 38.8889 | 1980.5556
154 | 0 | 0 | 0 | 1980.5556
155 | 0 | 0 | 0 | 1980.5556
156 | 0 | 0 | 0 | 1980.5556
157 | 0 | 0 | 0 | 1980.5556
158 | 0 | 0 | 0 | 1980.5556
159 | 0 | 0 | 0 | 1980.5556
160 | 0 | 0 | 0 | 1980.5556
161 | 0 | 0 | 0 | 1980.5556
162 | 0 | 0 | 0 | 1980.5556
163 | 0 | 0 | 0 | 1980.5556
164 | 0 | 0 | 0 | 1980.5556
165 | 0 | 0 | 0 | 1980.5556
166 | 0 | 0 | 0 | 1980.5556
167 | 0 | 0 | 0 | 1980.5556
168 | 0 | 0 | 0 | 1980.5556
169 | 0.48611 | 486.1111 | 97.2222 | 2077.7778
170 | 0 | 0 | 0 | 2077.7778
171 | 0 | 0 | 0 | 2077.7778
172 | 0 | 0 | 0 | 2077.7778
173 | 0 | 0 | 0 | 2077.7778
174 | 0.097222 | 97.2222 | 19.4444 | 2097.2222
175 | 0.93056 | 930.5556 | 186.1111 | 2283.3333
176 | 0.27778 | 277.7778 | 55.5556 | 2338.8889
177 | 0 | 0 | 0 | 2338.8889
178 | 0 | 0 | 0 | 2338.8889
179 | 0 | 0 | 0 | 2338.8889
180 | 0 | 0 | 0 | 2338.8889
181 | 0 | 0 | 0 | 2338.8889
182 | 0 | 0 | 0 | 2338.8889
183 | 0 | 0 | 0 | 2338.8889
184 | 0 | 0 | 0 | 2338.8889
185 | 0 | 0 | 0 | 2338.8889
186 | 0 | 0 | 0 | 2338.8889
187 | 0 | 0 | 0 | 2338.8889
188 | 0.013889 | 13.8889 | 2.7778 | 2341.6667
189 | 0 | 0 | 0 | 2341.6667
190 | 0.069444 | 69.4444 | 13.8889 | 2355.5556
191 | 0.083333 | 83.3333 | 16.6667 | 2372.2222
192 | 0.16667 | 166.6667 | 33.3333 | 2405.5556
193 | 0.27778 | 277.7778 | 55.5556 | 2461.1111
194 | 0 | 0 | 0 | 2461.1111
195 | 0 | 0 | 0 | 2461.1111
196 | 0 | 0 | 0 | 2461.1111
197 | 0 | 0 | 0 | 2461.1111
198 | 0 | 0 | 0 | 2461.1111
199 | 0 | 0 | 0 | 2461.1111
200 | 0 | 0 | 0 | 2461.1111
201 | 0.041667 | 41.6667 | 8.3333 | 2469.4444
202 | 0 | 0 | 0 | 2469.4444
203 | 0 | 0 | 0 | 2469.4444
204 | 0.58333 | 583.3333 | 116.6667 | 2586.1111
205 | 0.27778 | 277.7778 | 55.5556 | 2641.6667
206 | 0.29167 | 291.6667 | 58.3333 | 2700
207 | 0 | 0 | 0 | 2700
208 | 0 | 0 | 0 | 2700
209 | 0 | 0 | 0 | 2700
210 | 0 | 0 | 0 | 2700
211 | 0 | 0 | 0 | 2700
212 | 0 | 0 | 0 | 2700
213 | 0 | 0 | 0 | 2700
214 | 0 | 0 | 0 | 2700
215 | 0 | 0 | 0 | 2700
216 | 0 | 0 | 0 | 2700
217 | 0 | 0 | 0 | 2700
218 | 0.22222 | 222.2222 | 44.4444 | 2744.4444
219 | 1.0139 | 1013.8889 | 202.7778 | 2947.2222
220 | 1.0417 | 1041.6667 | 208.3333 | 155.5556 | 1
221 | 0.125 | 125 | 25 | 180.5556
222 | 0 | 0 | 0 | 180.5556
223 | 0 | 0 | 0 | 180.5556
224 | 0 | 0 | 0 | 180.5556
225 | 0 | 0 | 0 | 180.5556
226 | 0 | 0 | 0 | 180.5556
227 | 0 | 0 | 0 | 180.5556
228 | 0 | 0 | 0 | 180.5556
229 | 0 | 0 | 0 | 180.5556
230 | 0 | 0 | 0 | 180.5556
231 | 0 | 0 | 0 | 180.5556
232 | 0 | 0 | 0 | 180.5556
233 | 0 | 0 | 0 | 180.5556
234 | 0 | 0 | 0 | 180.5556
235 | 0 | 0 | 0 | 180.5556
236 | 0 | 0 | 0 | 180.5556
237 | 0 | 0 | 0 | 180.5556
238 | 0 | 0 | 0 | 180.5556
239 | 0.19444 | 194.4444 | 38.8889 | 219.4444
240 | 0.72222 | 722.2222 | 144.4444 | 363.8889
241 | 1.0417 | 1041.6667 | 208.3333 | 572.2222
242 | 1.0417 | 1041.6667 | 208.3333 | 780.5556
243 | 0.41667 | 416.6667 | 83.3333 | 863.8889
244 | 1.0417 | 1041.6667 | 208.3333 | 1072.2222
245 | 0.055556 | 55.5556 | 11.1111 | 1083.3333
246 | 0.16667 | 166.6667 | 33.3333 | 1116.6667
247 | 0 | 0 | 0 | 1116.6667
248 | 0.11111 | 111.1111 | 22.2222 | 1138.8889
249 | 0 | 0 | 0 | 1138.8889
250 | 1.0417 | 1041.6667 | 208.3333 | 1347.2222
251 | 0.90278 | 902.7778 | 180.5556 | 1527.7778
252 | 0.097222 | 97.2222 | 19.4444 | 1547.2222
253 | 0 | 0 | 0 | 1547.2222
254 | 0 | 0 | 0 | 1547.2222
255 | 0 | 0 | 0 | 1547.2222
256 | 0 | 0 | 0 | 1547.2222
257 | 0 | 0 | 0 | 1547.2222
258 | 0.13889 | 138.8889 | 27.7778 | 1575
259 | 0.27778 | 277.7778 | 55.5556 | 1630.5556
260 | 0.19444 | 194.4444 | 38.8889 | 1669.4444
261 | 1.0417 | 1041.6667 | 208.3333 | 1877.7778
262 | 1.0417 | 1041.6667 | 208.3333 | 2086.1111
263 | 0.097222 | 97.2222 | 19.4444 | 2105.5556
264 | 0.29167 | 291.6667 | 58.3333 | 2163.8889
265 | 1.0417 | 1041.6667 | 208.3333 | 2372.2222
266 | 1.0417 | 1041.6667 | 208.3333 | 2580.5556
267 | 0.81944 | 819.4444 | 163.8889 | 2744.4444
268 | 0.11111 | 111.1111 | 22.2222 | 2766.6667
269 | 0 | 0 | 0 | 2766.6667
270 | 0 | 0 | 0 | 2766.6667
271 | 0 | 0 | 0 | 2766.6667
272 | 0 | 0 | 0 | 2766.6667
273 | 0 | 0 | 0 | 2766.6667
274 | 0 | 0 | 0 | 2766.6667
275 | 0 | 0 | 0 | 2766.6667
276 | 0 | 0 | 0 | 2766.6667
277 | 0 | 0 | 0 | 2766.6667
278 | 0 | 0 | 0 | 2766.6667
279 | 0.27778 | 277.7778 | 55.5556 | 2822.2222
280 | 1.0417 | 1041.6667 | 208.3333 | 30.5556 | 1
281 | 0.63889 | 638.8889 | 127.7778 | 158.3333
282 | 1.0417 | 1041.6667 | 208.3333 | 366.6667
283 | 1.0417 | 1041.6667 | 208.3333 | 575
284 | 1.0417 | 1041.6667 | 208.3333 | 783.3333
285 | 0.055556 | 55.5556 | 11.1111 | 794.4444
286 | 0.041667 | 41.6667 | 8.3333 | 802.7778
287 | 0 | 0 | 0 | 802.7778
288 | 0 | 0 | 0 | 802.7778
289 | 0.98611 | 986.1111 | 197.2222 | 1000
290 | 0.44444 | 444.4444 | 88.8889 | 1088.8889
291 | 1.0417 | 1041.6667 | 208.3333 | 1297.2222
292 | 0.041667 | 41.6667 | 8.3333 | 1305.5556
293 | 0.70833 | 708.3333 | 141.6667 | 1447.2222
294 | 0.27778 | 277.7778 | 55.5556 | 1502.7778
295 | 0.68056 | 680.5556 | 136.1111 | 1638.8889
296 | 0 | 0 | 0 | 1638.8889
297 | 0.40278 | 402.7778 | 80.5556 | 1719.4444
298 | 0.27778 | 277.7778 | 55.5556 | 1775
299 | 0 | 0 | 0 | 1775
300 | 0.47222 | 472.2222 | 94.4444 | 1869.4444
301 | 1.0417 | 1041.6667 | 208.3333 | 2077.7778
302 | 1.0417 | 1041.6667 | 208.3333 | 2286.1111
303 | 1.0417 | 1041.6667 | 208.3333 | 2494.4444
304 | 1.0417 | 1041.6667 | 208.3333 | 2702.7778
305 | 0.083333 | 83.3333 | 16.6667 | 2719.4444
306 | 0 | 0 | 0 | 2719.4444
307 | 0 | 0 | 0 | 2719.4444
308 | 0.23611 | 236.1111 | 47.2222 | 2766.6667
309 | 0.41667 | 416.6667 | 83.3333 | 2850
310 | 1.0417 | 1041.6667 | 208.3333 | 58.3333 | 1
311 | 0.15278 | 152.7778 | 30.5556 | 88.8889
312 | 0.11111 | 111.1111 | 22.2222 | 111.1111
313 | 0 | 0 | 0 | 111.1111
314 | 1.0417 | 1041.6667 | 208.3333 | 319.4444
315 | 1.0417 | 1041.6667 | 208.3333 | 527.7778
316 | 1.0417 | 1041.6667 | 208.3333 | 736.1111
317 | 0.79167 | 791.6667 | 158.3333 | 894.4444
318 | 0.041667 | 41.6667 | 8.3333 | 902.7778
319 | 0.41667 | 416.6667 | 83.3333 | 986.1111
320 | 1.0417 | 1041.6667 | 208.3333 | 1194.4444
321 | 0.43056 | 430.5556 | 86.1111 | 1280.5556
322 | 0 | 0 | 0 | 1280.5556
323 | 0 | 0 | 0 | 1280.5556
324 | 0 | 0 | 0 | 1280.5556
325 | 0 | 0 | 0 | 1280.5556
326 | 0 | 0 | 0 | 1280.5556
327 | 0 | 0 | 0 | 1280.5556
328 | 0 | 0 | 0 | 1280.5556
329 | 0 | 0 | 0 | 1280.5556
330 | 0 | 0 | 0 | 1280.5556
331 | 0 | 0 | 0 | 1280.5556
332 | 0 | 0 | 0 | 1280.5556
333 | 0 | 0 | 0 | 1280.5556
334 | 0.90278 | 902.7778 | 180.5556 | 1461.1111
335 | 1.0417 | 1041.6667 | 208.3333 | 1669.4444
336 | 1.0417 | 1041.6667 | 208.3333 | 1877.7778
337 | 1.0417 | 1041.6667 | 208.3333 | 2086.1111
338 | 1.0417 | 1041.6667 | 208.3333 | 2294.4444
339 | 1.0417 | 1041.6667 | 208.3333 | 2502.7778
340 | 1.0417 | 1041.6667 | 208.3333 | 2711.1111
341 | 1.0417 | 1041.6667 | 208.3333 | 2919.4444
342 | 1.0417 | 1041.6667 | 208.3333 | 127.7778 | 1
343 | 0.33333 | 333.3333 | 66.6667 | 194.4444
344 | 0.84722 | 847.2222 | 169.4444 | 363.8889
345 | 0.23611 | 236.1111 | 47.2222 | 411.1111
346 | 1.0417 | 1041.6667 | 208.3333 | 619.4444
347 | 0 | 0 | 0 | 619.4444
348 | 0.16667 | 166.6667 | 33.3333 | 652.7778
349 | 0.20833 | 208.3333 | 41.6667 | 694.4444
350 | 0.15278 | 152.7778 | 30.5556 | 725
351 | 1.0417 | 1041.6667 | 208.3333 | 933.3333
352 | 1.0417 | 1041.6667 | 208.3333 | 1141.6667
353 | 1.0417 | 1041.6667 | 208.3333 | 1350
354 | 1.0417 | 1041.6667 | 208.3333 | 1558.3333
355 | 0.625 | 625 | 125 | 1683.3333
356 | 1.0417 | 1041.6667 | 208.3333 | 1891.6667
357 | 0.65278 | 652.7778 | 130.5556 | 2022.2222
358 | 0 | 0 | 0 | 2022.2222
359 | 0 | 0 | 0 | 2022.2222
360 | 1.0417 | 1041.6667 | 208.3333 | 2230.5556
361 | 0.11111 | 111.1111 | 22.2222 | 2252.7778
362 | 0.013889 | 13.8889 | 2.7778 | 2255.5556
363 | 0 | 0 | 0 | 2255.5556
364 | 0 | 0 | 0 | 2255.5556
365 | 0 | 0 | 0 | 2255.5556
366 | 0 | 0 | 0 | 2255.5556

## Chlorine Filter
Contact Time | 10 | min |  | Chlorine Total |  | Maintainence Total | COSTS
Solution Concentration | 5 | % |  | 23172.6667 | g | 7 | Initial Cost | 700 | $
CT_Chlorine | 100 | mg * min / L |  | 23.1727 | Kg |  | Maintainence Cost | 100 | $
Refill Amount | 3 | Kg
| Q_in | Q_in | Chlorine Mass | Mass Total | Counter
| [L/min] | L / Day | [g] | [g]
1 | 0.54167 | 780 | 156 | 156
2 | 0.069444 | 69.4444 | 13.8889 | 169.8889
3 | 0.93056 | 930.5556 | 186.1111 | 356
4 | 1.0417 | 1041.6667 | 208.3333 | 564.3333
5 | 1.0417 | 1041.6667 | 208.3333 | 772.6667
6 | 0.19444 | 194.4444 | 38.8889 | 811.5556
7 | 0 | 0 | 0 | 811.5556
8 | 0 | 0 | 0 | 811.5556
9 | 0.055556 | 55.5556 | 11.1111 | 822.6667
10 | 0 | 0 | 0 | 822.6667
11 | 0 | 0 | 0 | 822.6667
12 | 0 | 0 | 0 | 822.6667
13 | 0 | 0 | 0 | 822.6667
14 | 0.027778 | 27.7778 | 5.5556 | 828.2222
15 | 1.0417 | 1041.6667 | 208.3333 | 1036.5556
16 | 0.41667 | 416.6667 | 83.3333 | 1119.8889
17 | 1.0417 | 1041.6667 | 208.3333 | 1328.2222
18 | 1.0417 | 1041.6667 | 208.3333 | 1536.5556
19 | 0.18056 | 180.5556 | 36.1111 | 1572.6667
20 | 0.027778 | 27.7778 | 5.5556 | 1578.2222
21 | 1.0417 | 1041.6667 | 208.3333 | 1786.5556
22 | 0.97222 | 972.2222 | 194.4444 | 1981
23 | 1.0417 | 1041.6667 | 208.3333 | 2189.3333
24 | 1.0417 | 1041.6667 | 208.3333 | 2397.6667
25 | 0.125 | 125 | 25 | 2422.6667
26 | 0.19444 | 194.4444 | 38.8889 | 2461.5556
27 | 0.19444 | 194.4444 | 38.8889 | 2500.4444
28 | 0 | 0 | 0 | 2500.4444
29 | 0 | 0 | 0 | 2500.4444
30 | 0.041667 | 41.6667 | 8.3333 | 2508.7778
31 | 0.40278 | 402.7778 | 80.5556 | 2589.3333
32 | 0.55556 | 555.5556 | 111.1111 | 2700.4444
33 | 1.0417 | 1041.6667 | 208.3333 | 2908.7778
34 | 0.041667 | 41.6667 | 8.3333 | 2917.1111
35 | 1.0417 | 1041.6667 | 208.3333 | 208.3333 | 1
36 | 1.0417 | 1041.6667 | 208.3333 | 416.6667
37 | 1.0417 | 1041.6667 | 208.3333 | 625
38 | 1.0417 | 1041.6667 | 208.3333 | 833.3333
39 | 0.45833 | 458.3333 | 91.6667 | 925
40 | 0.22222 | 222.2222 | 44.4444 | 969.4444
41 | 0.013889 | 13.8889 | 2.7778 | 972.2222
42 | 1.0417 | 1041.6667 | 208.3333 | 1180.5556
43 | 1.0417 | 1041.6667 | 208.3333 | 1388.8889
44 | 1.0417 | 1041.6667 | 208.3333 | 1597.2222
45 | 0.013889 | 13.8889 | 2.7778 | 1600
46 | 0 | 0 | 0 | 1600
47 | 0 | 0 | 0 | 1600
48 | 0 | 0 | 0 | 1600
49 | 0.27778 | 277.7778 | 55.5556 | 1655.5556
50 | 0.76389 | 763.8889 | 152.7778 | 1808.3333
51 | 0.027778 | 27.7778 | 5.5556 | 1813.8889
52 | 0 | 0 | 0 | 1813.8889
53 | 0 | 0 | 0 | 1813.8889
54 | 0 | 0 | 0 | 1813.8889
55 | 0.013889 | 13.8889 | 2.7778 | 1816.6667
56 | 0.31944 | 319.4444 | 63.8889 | 1880.5556
57 | 0.61111 | 611.1111 | 122.2222 | 2002.7778
58 | 0.027778 | 27.7778 | 5.5556 | 2008.3333
59 | 0 | 0 | 0 | 2008.3333
60 | 0.083333 | 83.3333 | 16.6667 | 2025
61 | 0 | 0 | 0 | 2025
62 | 0 | 0 | 0 | 2025
63 | 0.027778 | 27.7778 | 5.5556 | 2030.5556
64 | 0.125 | 125 | 25 | 2055.5556
65 | 0.055556 | 55.5556 | 11.1111 | 2066.6667
66 | 0 | 0 | 0 | 2066.6667
67 | 0.027778 | 27.7778 | 5.5556 | 2072.2222
68 | 0.027778 | 27.7778 | 5.5556 | 2077.7778
69 | 0.19444 | 194.4444 | 38.8889 | 2116.6667
70 | 0.94444 | 944.4444 | 188.8889 | 2305.5556
71 | 0.59722 | 597.2222 | 119.4444 | 2425
72 | 1.0417 | 1041.6667 | 208.3333 | 2633.3333
73 | 0.041667 | 41.6667 | 8.3333 | 2641.6667
74 | 0 | 0 | 0 | 2641.6667
75 | 0 | 0 | 0 | 2641.6667
76 | 0 | 0 | 0 | 2641.6667
77 | 1.0417 | 1041.6667 | 208.3333 | 2850
78 | 1.0417 | 1041.6667 | 208.3333 | 208.3333 | 1
79 | 1.0417 | 1041.6667 | 208.3333 | 416.6667
80 | 0 | 0 | 0 | 416.6667
81 | 0.48611 | 486.1111 | 97.2222 | 513.8889
82 | 0.66667 | 666.6667 | 133.3333 | 647.2222
83 | 1.0417 | 1041.6667 | 208.3333 | 855.5556
84 | 1.0417 | 1041.6667 | 208.3333 | 1063.8889
85 | 1.0417 | 1041.6667 | 208.3333 | 1272.2222
86 | 1.0417 | 1041.6667 | 208.3333 | 1480.5556
87 | 1.0417 | 1041.6667 | 208.3333 | 1688.8889
88 | 0.69444 | 694.4444 | 138.8889 | 1827.7778
89 | 1.0417 | 1041.6667 | 208.3333 | 2036.1111
90 | 0.80556 | 805.5556 | 161.1111 | 2197.2222
91 | 0 | 0 | 0 | 2197.2222
92 | 1.0417 | 1041.6667 | 208.3333 | 2405.5556
93 | 0.625 | 625 | 125 | 2530.5556
94 | 0.58333 | 583.3333 | 116.6667 | 2647.2222
95 | 0.041667 | 41.6667 | 8.3333 | 2655.5556
96 | 0 | 0 | 0 | 2655.5556
97 | 0 | 0 | 0 | 2655.5556
98 | 0 | 0 | 0 | 2655.5556
99 | 0.22222 | 222.2222 | 44.4444 | 2700
100 | 1.0417 | 1041.6667 | 208.3333 | 2908.3333
101 | 0.63889 | 638.8889 | 127.7778 | 127.7778 | 1
102 | 1.0417 | 1041.6667 | 208.3333 | 336.1111
103 | 1.0417 | 1041.6667 | 208.3333 | 544.4444
104 | 0.10417 | 104.1667 | 20.8333 | 565.2778
105 | 1.0417 | 1041.6667 | 208.3333 | 773.6111
106 | 0.20833 | 208.3333 | 41.6667 | 815.2778
107 | 0 | 0 | 0 | 815.2778
108 | 0 | 0 | 0 | 815.2778
109 | 0 | 0 | 0 | 815.2778
110 | 0.076389 | 76.3889 | 15.2778 | 830.5556
111 | 0.027778 | 27.7778 | 5.5556 | 836.1111
112 | 0.56944 | 569.4444 | 113.8889 | 950
113 | 0.58333 | 583.3333 | 116.6667 | 1066.6667
114 | 0.125 | 125 | 25 | 1091.6667
115 | 0 | 0 | 0 | 1091.6667
116 | 0.29167 | 291.6667 | 58.3333 | 1150
117 | 1.0417 | 1041.6667 | 208.3333 | 1358.3333
118 | 1.0417 | 1041.6667 | 208.3333 | 1566.6667
119 | 1.0417 | 1041.6667 | 208.3333 | 1775
120 | 0.33333 | 333.3333 | 66.6667 | 1841.6667
121 | 0.055556 | 55.5556 | 11.1111 | 1852.7778
122 | 0 | 0 | 0 | 1852.7778
123 | 0 | 0 | 0 | 1852.7778
124 | 1.0417 | 1041.6667 | 208.3333 | 2061.1111
125 | 0.027778 | 27.7778 | 5.5556 | 2066.6667
126 | 0 | 0 | 0 | 2066.6667
127 | 0 | 0 | 0 | 2066.6667
128 | 0 | 0 | 0 | 2066.6667
129 | 0 | 0 | 0 | 2066.6667
130 | 0.027778 | 27.7778 | 5.5556 | 2072.2222
131 | 0 | 0 | 0 | 2072.2222
132 | 0 | 0 | 0 | 2072.2222
133 | 0 | 0 | 0 | 2072.2222
134 | 0 | 0 | 0 | 2072.2222
135 | 0 | 0 | 0 | 2072.2222
136 | 0.013889 | 13.8889 | 2.7778 | 2075
137 | 0 | 0 | 0 | 2075
138 | 0 | 0 | 0 | 2075
139 | 0 | 0 | 0 | 2075
140 | 0 | 0 | 0 | 2075
141 | 0 | 0 | 0 | 2075
142 | 0.013889 | 13.8889 | 2.7778 | 2077.7778
143 | 0.013889 | 13.8889 | 2.7778 | 2080.5556
144 | 0 | 0 | 0 | 2080.5556
145 | 0 | 0 | 0 | 2080.5556
146 | 0 | 0 | 0 | 2080.5556
147 | 0 | 0 | 0 | 2080.5556
148 | 0 | 0 | 0 | 2080.5556
149 | 0 | 0 | 0 | 2080.5556
150 | 0 | 0 | 0 | 2080.5556
151 | 0 | 0 | 0 | 2080.5556
152 | 0.51389 | 513.8889 | 102.7778 | 2183.3333
153 | 0.19444 | 194.4444 | 38.8889 | 2222.2222
154 | 0 | 0 | 0 | 2222.2222
155 | 0 | 0 | 0 | 2222.2222
156 | 0 | 0 | 0 | 2222.2222
157 | 0 | 0 | 0 | 2222.2222
158 | 0 | 0 | 0 | 2222.2222
159 | 0 | 0 | 0 | 2222.2222
160 | 0 | 0 | 0 | 2222.2222
161 | 0 | 0 | 0 | 2222.2222
162 | 0 | 0 | 0 | 2222.2222
163 | 0 | 0 | 0 | 2222.2222
164 | 0 | 0 | 0 | 2222.2222
165 | 0 | 0 | 0 | 2222.2222
166 | 0 | 0 | 0 | 2222.2222
167 | 0 | 0 | 0 | 2222.2222
168 | 0 | 0 | 0 | 2222.2222
169 | 0.48611 | 486.1111 | 97.2222 | 2319.4444
170 | 0 | 0 | 0 | 2319.4444
171 | 0 | 0 | 0 | 2319.4444
172 | 0 | 0 | 0 | 2319.4444
173 | 0 | 0 | 0 | 2319.4444
174 | 0.097222 | 97.2222 | 19.4444 | 2338.8889
175 | 0.93056 | 930.5556 | 186.1111 | 2525
176 | 0.27778 | 277.7778 | 55.5556 | 2580.5556
177 | 0 | 0 | 0 | 2580.5556
178 | 0 | 0 | 0 | 2580.5556
179 | 0 | 0 | 0 | 2580.5556
180 | 0 | 0 | 0 | 2580.5556
181 | 0 | 0 | 0 | 2580.5556
182 | 0 | 0 | 0 | 2580.5556
183 | 0 | 0 | 0 | 2580.5556
184 | 0 | 0 | 0 | 2580.5556
185 | 0 | 0 | 0 | 2580.5556
186 | 0 | 0 | 0 | 2580.5556
187 | 0 | 0 | 0 | 2580.5556
188 | 0.013889 | 13.8889 | 2.7778 | 2583.3333
189 | 0 | 0 | 0 | 2583.3333
190 | 0.069444 | 69.4444 | 13.8889 | 2597.2222
191 | 0.083333 | 83.3333 | 16.6667 | 2613.8889
192 | 0.16667 | 166.6667 | 33.3333 | 2647.2222
193 | 0.27778 | 277.7778 | 55.5556 | 2702.7778
194 | 0 | 0 | 0 | 2702.7778
195 | 0 | 0 | 0 | 2702.7778
196 | 0 | 0 | 0 | 2702.7778
197 | 0 | 0 | 0 | 2702.7778
198 | 0 | 0 | 0 | 2702.7778
199 | 0 | 0 | 0 | 2702.7778
200 | 0 | 0 | 0 | 2702.7778
201 | 0.041667 | 41.6667 | 8.3333 | 2711.1111
202 | 0 | 0 | 0 | 2711.1111
203 | 0 | 0 | 0 | 2711.1111
204 | 0.58333 | 583.3333 | 116.6667 | 2827.7778
205 | 0.27778 | 277.7778 | 55.5556 | 2883.3333
206 | 0.29167 | 291.6667 | 58.3333 | 2941.6667
207 | 0 | 0 | 0 | 2941.6667
208 | 0 | 0 | 0 | 2941.6667
209 | 0 | 0 | 0 | 2941.6667
210 | 0 | 0 | 0 | 2941.6667
211 | 0 | 0 | 0 | 2941.6667
212 | 0 | 0 | 0 | 2941.6667
213 | 0 | 0 | 0 | 2941.6667
214 | 0 | 0 | 0 | 2941.6667
215 | 0 | 0 | 0 | 2941.6667
216 | 0 | 0 | 0 | 2941.6667
217 | 0 | 0 | 0 | 2941.6667
218 | 0.22222 | 222.2222 | 44.4444 | 2986.1111
219 | 1.0139 | 1013.8889 | 202.7778 | 202.7778 | 1
220 | 1.0417 | 1041.6667 | 208.3333 | 411.1111
221 | 0.125 | 125 | 25 | 436.1111
222 | 0 | 0 | 0 | 436.1111
223 | 0 | 0 | 0 | 436.1111
224 | 0 | 0 | 0 | 436.1111
225 | 0 | 0 | 0 | 436.1111
226 | 0 | 0 | 0 | 436.1111
227 | 0 | 0 | 0 | 436.1111
228 | 0 | 0 | 0 | 436.1111
229 | 0 | 0 | 0 | 436.1111
230 | 0 | 0 | 0 | 436.1111
231 | 0 | 0 | 0 | 436.1111
232 | 0 | 0 | 0 | 436.1111
233 | 0 | 0 | 0 | 436.1111
234 | 0 | 0 | 0 | 436.1111
235 | 0 | 0 | 0 | 436.1111
236 | 0 | 0 | 0 | 436.1111
237 | 0 | 0 | 0 | 436.1111
238 | 0 | 0 | 0 | 436.1111
239 | 0.19444 | 194.4444 | 38.8889 | 475
240 | 0.72222 | 722.2222 | 144.4444 | 619.4444
241 | 1.0417 | 1041.6667 | 208.3333 | 827.7778
242 | 1.0417 | 1041.6667 | 208.3333 | 1036.1111
243 | 0.41667 | 416.6667 | 83.3333 | 1119.4444
244 | 1.0417 | 1041.6667 | 208.3333 | 1327.7778
245 | 0.055556 | 55.5556 | 11.1111 | 1338.8889
246 | 0.16667 | 166.6667 | 33.3333 | 1372.2222
247 | 0 | 0 | 0 | 1372.2222
248 | 0.11111 | 111.1111 | 22.2222 | 1394.4444
249 | 0 | 0 | 0 | 1394.4444
250 | 1.0417 | 1041.6667 | 208.3333 | 1602.7778
251 | 0.90278 | 902.7778 | 180.5556 | 1783.3333
252 | 0.097222 | 97.2222 | 19.4444 | 1802.7778
253 | 0 | 0 | 0 | 1802.7778
254 | 0 | 0 | 0 | 1802.7778
255 | 0 | 0 | 0 | 1802.7778
256 | 0 | 0 | 0 | 1802.7778
257 | 0 | 0 | 0 | 1802.7778
258 | 0.13889 | 138.8889 | 27.7778 | 1830.5556
259 | 0.27778 | 277.7778 | 55.5556 | 1886.1111
260 | 0.19444 | 194.4444 | 38.8889 | 1925
261 | 1.0417 | 1041.6667 | 208.3333 | 2133.3333
262 | 1.0417 | 1041.6667 | 208.3333 | 2341.6667
263 | 0.097222 | 97.2222 | 19.4444 | 2361.1111
264 | 0.29167 | 291.6667 | 58.3333 | 2419.4444
265 | 1.0417 | 1041.6667 | 208.3333 | 2627.7778
266 | 1.0417 | 1041.6667 | 208.3333 | 2836.1111
267 | 0.81944 | 819.4444 | 163.8889 | 3000
268 | 0.11111 | 111.1111 | 22.2222 | 22.2222 | 1
269 | 0 | 0 | 0 | 22.2222
270 | 0 | 0 | 0 | 22.2222
271 | 0 | 0 | 0 | 22.2222
272 | 0 | 0 | 0 | 22.2222
273 | 0 | 0 | 0 | 22.2222
274 | 0 | 0 | 0 | 22.2222
275 | 0 | 0 | 0 | 22.2222
276 | 0 | 0 | 0 | 22.2222
277 | 0 | 0 | 0 | 22.2222
278 | 0 | 0 | 0 | 22.2222
279 | 0.27778 | 277.7778 | 55.5556 | 77.7778
280 | 1.0417 | 1041.6667 | 208.3333 | 286.1111
281 | 0.63889 | 638.8889 | 127.7778 | 413.8889
282 | 1.0417 | 1041.6667 | 208.3333 | 622.2222
283 | 1.0417 | 1041.6667 | 208.3333 | 830.5556
284 | 1.0417 | 1041.6667 | 208.3333 | 1038.8889
285 | 0.055556 | 55.5556 | 11.1111 | 1050
286 | 0.041667 | 41.6667 | 8.3333 | 1058.3333
287 | 0 | 0 | 0 | 1058.3333
288 | 0 | 0 | 0 | 1058.3333
289 | 0.98611 | 986.1111 | 197.2222 | 1255.5556
290 | 0.44444 | 444.4444 | 88.8889 | 1344.4444
291 | 1.0417 | 1041.6667 | 208.3333 | 1552.7778
292 | 0.041667 | 41.6667 | 8.3333 | 1561.1111
293 | 0.70833 | 708.3333 | 141.6667 | 1702.7778
294 | 0.27778 | 277.7778 | 55.5556 | 1758.3333
295 | 0.68056 | 680.5556 | 136.1111 | 1894.4444
296 | 0 | 0 | 0 | 1894.4444
297 | 0.40278 | 402.7778 | 80.5556 | 1975
298 | 0.27778 | 277.7778 | 55.5556 | 2030.5556
299 | 0 | 0 | 0 | 2030.5556
300 | 0.47222 | 472.2222 | 94.4444 | 2125
301 | 1.0417 | 1041.6667 | 208.3333 | 2333.3333
302 | 1.0417 | 1041.6667 | 208.3333 | 2541.6667
303 | 1.0417 | 1041.6667 | 208.3333 | 2750
304 | 1.0417 | 1041.6667 | 208.3333 | 2958.3333
305 | 0.083333 | 83.3333 | 16.6667 | 2975
306 | 0 | 0 | 0 | 2975
307 | 0 | 0 | 0 | 2975
308 | 0.23611 | 236.1111 | 47.2222 | 47.2222 | 1
309 | 0.41667 | 416.6667 | 83.3333 | 130.5556
310 | 1.0417 | 1041.6667 | 208.3333 | 338.8889
311 | 0.15278 | 152.7778 | 30.5556 | 369.4444
312 | 0.11111 | 111.1111 | 22.2222 | 391.6667
313 | 0 | 0 | 0 | 391.6667
314 | 1.0417 | 1041.6667 | 208.3333 | 600
315 | 1.0417 | 1041.6667 | 208.3333 | 808.3333
316 | 1.0417 | 1041.6667 | 208.3333 | 1016.6667
317 | 0.79167 | 791.6667 | 158.3333 | 1175
318 | 0.041667 | 41.6667 | 8.3333 | 1183.3333
319 | 0.41667 | 416.6667 | 83.3333 | 1266.6667
320 | 1.0417 | 1041.6667 | 208.3333 | 1475
321 | 0.43056 | 430.5556 | 86.1111 | 1561.1111
322 | 0 | 0 | 0 | 1561.1111
323 | 0 | 0 | 0 | 1561.1111
324 | 0 | 0 | 0 | 1561.1111
325 | 0 | 0 | 0 | 1561.1111
326 | 0 | 0 | 0 | 1561.1111
327 | 0 | 0 | 0 | 1561.1111
328 | 0 | 0 | 0 | 1561.1111
329 | 0 | 0 | 0 | 1561.1111
330 | 0 | 0 | 0 | 1561.1111
331 | 0 | 0 | 0 | 1561.1111
332 | 0 | 0 | 0 | 1561.1111
333 | 0 | 0 | 0 | 1561.1111
334 | 0.90278 | 902.7778 | 180.5556 | 1741.6667
335 | 1.0417 | 1041.6667 | 208.3333 | 1950
336 | 1.0417 | 1041.6667 | 208.3333 | 2158.3333
337 | 1.0417 | 1041.6667 | 208.3333 | 2366.6667
338 | 1.0417 | 1041.6667 | 208.3333 | 2575
339 | 1.0417 | 1041.6667 | 208.3333 | 2783.3333
340 | 1.0417 | 1041.6667 | 208.3333 | 2991.6667
341 | 1.0417 | 1041.6667 | 208.3333 | 208.3333 | 1
342 | 1.0417 | 1041.6667 | 208.3333 | 416.6667
343 | 0.33333 | 333.3333 | 66.6667 | 483.3333
344 | 0.84722 | 847.2222 | 169.4444 | 652.7778
345 | 0.23611 | 236.1111 | 47.2222 | 700
346 | 1.0417 | 1041.6667 | 208.3333 | 908.3333
347 | 0 | 0 | 0 | 908.3333
348 | 0.16667 | 166.6667 | 33.3333 | 941.6667
349 | 0.20833 | 208.3333 | 41.6667 | 983.3333
350 | 0.15278 | 152.7778 | 30.5556 | 1013.8889
351 | 1.0417 | 1041.6667 | 208.3333 | 1222.2222
352 | 1.0417 | 1041.6667 | 208.3333 | 1430.5556
353 | 1.0417 | 1041.6667 | 208.3333 | 1638.8889
354 | 1.0417 | 1041.6667 | 208.3333 | 1847.2222
355 | 0.625 | 625 | 125 | 1972.2222
356 | 1.0417 | 1041.6667 | 208.3333 | 2180.5556
357 | 0.65278 | 652.7778 | 130.5556 | 2311.1111
358 | 0 | 0 | 0 | 2311.1111
359 | 0 | 0 | 0 | 2311.1111
360 | 1.0417 | 1041.6667 | 208.3333 | 2519.4444
361 | 0.11111 | 111.1111 | 22.2222 | 2541.6667
362 | 0.013889 | 13.8889 | 2.7778 | 2544.4444
363 | 0 | 0 | 0 | 2544.4444
364 | 0 | 0 | 0 | 2544.4444
365 | 0 | 0 | 0 | 2544.4444
366 | 0 | 0 | 0 | 2544.4444

## Updated Pump Parameters
Distance to Tank | 63.9316 | [m] |  | Pump coefficient a | -0.0151 |  | Diameter of Pipe | 20 | [mm]
Height of storage tank | 21.5 | [m] |  | Pump coefficient b | -0.5516 |  | Friction factor f | 0.05 | N/A
Density of water | 1000 | [kg/m^3] |  | Pump coefficient c | 356.8 |  | Loss coeffecient K | 8 | N/A | Filter Line | Up
Gravity | 9.81 | [m/s^2] |  | Pump Selected | Pump C |  | Filter coeffecient C | 3827.2288 | N/A
[7 empty] | Cross Area of Pipe | 0.00031416 | [m^2]
Flow velocity v | Flow Rate Q | Pump Pressure p-pump | System Curve Pressure p-system | Pressure | Friction | Loss | Filter
[m/s] | [L/min] | [kPa] | [kPa] | [Pa | [Pa] | [Pa} | [Pa]
0 | 0 | 356.8 | 210.915 | 210915 | 0 | 0 | 0
0.2 | 3.7699 | 354.5059 | 215.037 | 210915 | 3196.5802 | 160 | 765.4458
0.4 | 7.5398 | 351.7826 | 225.8722 | 210915 | 12786.3208 | 640 | 1530.8915
0.6 | 11.3097 | 348.6301 | 243.4206 | 210915 | 28769.2218 | 1440 | 2296.3373
0.8 | 15.0796 | 345.0484 | 267.6821 | 210915 | 51145.2833 | 2560 | 3061.783
1 | 18.8496 | 341.0375 | 298.6567 | 210915 | 79914.5051 | 4000 | 3827.2288
1.2 | 22.6195 | 336.5973 | 336.3446 | 210915 | 115076.8873 | 5760 | 4592.6746
1.4 | 26.3894 | 331.728 | 380.7456 | 210915 | 156632.43 | 7840 | 5358.1203
1.6 | 30.1593 | 326.4294 | 431.8597 | 210915 | 204581.133 | 10240 | 6123.5661
1.8 | 33.9292 | 320.7017 | 489.687 | 210915 | 258922.9965 | 12960 | 6889.0118
2 | 37.6991 | 314.5447 | 554.2275 | 210915 | 319658.0204 | 16000 | 7654.4576
2.2 | 41.469 | 307.9585 | 625.4811 | 210915 | 386786.2047 | 19360 | 8419.9034
2.4 | 45.2389 | 300.9431 | 703.4479 | 210915 | 460307.5494 | 23040 | 9185.3491
2.6 | 49.0088 | 293.4985 | 788.1278 | 210915 | 540222.0545 | 27040 | 9950.7949
2.8 | 52.7788 | 285.6247 | 879.521 | 210915 | 626529.72 | 31360 | 10716.2406
3 | 56.5487 | 277.3217 | 977.6272 | 210915 | 719230.5459 | 36000 | 11481.6864
|  | Pump Pressure [kPa] | 336.5716 | Quadratic Equation Solver
|  | Flow Rate [L/min] | 22.6403 | A | -0.25128
|  |  |  | B | -0.75464
|  |  |  | C | 145.885
|  |  |  | Q1 | -25.6436 | L/min
|  |  |  | Q2 | 22.6403 | L/min
|  |  |  | v |  | m/s
|  |  |  | Q | 22.6403 | L/min

## W11 Filter Loss Coefficient Exp
| Experiment 1 Constants |  |  |  | Calculated Filter Resistance Coefficient |  |  |  | Experiment 2 Constants
| Inner Pipe Diameter (D) | 1 | [cm] |  | C_f,exp | 15040 | [ ] |  | Length (L) | 1.22 | [m]
| Pipe Cross-Sectional Area (A) | 7.854e-05 | [m^2] | [5 empty] | Power (P) | 2.19 | [W]
| Water Density (ρ) | 1000 | [kg/m^3]
| Gravitational Acceleration (g) | 9.81 | [m/s^2]
| Tubing Length (L) | 2.664 | [m]
# | Initial Water Level | Height of Filter Level | Height Difference (h) | Pressure (ρgh) | Collected Volume | Time | Flow Rate | Velocity | Height | Volume | Time | Flow Rate | Efficiency | Height of Thing | Height Difference
| [m] | [m] | [m] | [Pa] | [mL] | [s] | [LPM] | [m/s] | [m] | [mL] | [s] | [LPM] | [%] | [m] | [m]
1 | 0 | 0.3 | 0.3 | 2943 | 100 | 17.03 | 0.35232 | 0.074765 | 0 | 200 | 14.66 | 0.81855 | 2.6767 | 0.02 | 0.02
2 | 0 | 0.4 | 0.4 | 3924 | 100 | 14.02 | 0.42796 | 0.090816 | 500mL mark of graduated cylinder | 200 | 18.18 | 0.66007 | #VALUE! | 0.02 | #VALUE!
3 | 0 | 0.5 | 0.5 | 4905 | 100 | 12.07 | 0.4971 | 0.10549
4 | 0 | 0.9 | 0.9 | 8829 | 200 | 17.7 | 0.67797 | 0.14387
5 | 0 | 1 | 1 | 9810 | 200 | 16.31 | 0.73574 | 0.15613
Graph Data
Velocity [m/s] | Pressure [Pa]
0.074765 | 2943
0.090816 | 3924
0.10549 | 4905
0.14387 | 8829
0.15613 | 9810